## PA_Power
|  | Unit | Week #1 | [6 empty] | Week #2 | [6 empty] | Week #3 | [6 empty] | Week #4 | [6 empty] | Week #5 | [6 empty] | Week #6 | [6 empty] | Week #7 | [6 empty] | Week #8 | [6 empty] | Week #9 | [6 empty] | Week #10 | [6 empty] | Week #11 | [6 empty] | Week #12 | [6 empty] | Week #13 | [6 empty] | Week #14 | [6 empty] | Week #15 | [6 empty] | Week #16 | [6 empty] | Week #17 | [6 empty] | Week #18 | [6 empty] | Week #19 | [6 empty] | Week #20 | [6 empty] | Week #21 | [6 empty] | Week #22 | [6 empty] | Week #23 | [6 empty] | Week #24 | [6 empty] | Week #25 | [6 empty] | Week #26 | [6 empty] | Week #27 | [6 empty] | Week #28 | [6 empty] | Week #29 | [6 empty] | Week #30 | [6 empty] | Week #31 | [6 empty] | Week #32 | [6 empty] | Week #33 | [6 empty] | Week #34 | [6 empty] | Week #35 | [6 empty] | Week #36 | [6 empty] | Week #37 | [6 empty] | Week #38 | [6 empty] | Week #39 | [6 empty] | Week #40 | [6 empty] | Week #41 | [6 empty] | Week #42 | [6 empty] | Week #43 | [6 empty] | Week #44 | [6 empty] | Week #45 | [6 empty] | Week #46 | [6 empty] | Week #47 | [6 empty] | Week #48 | [6 empty] | Week #49 | [6 empty] | Week #50 | [6 empty] | Week #51 | [6 empty] | Week #52 | [6 empty] | Week #53
 | time axis 2020-12-26 to 2021-12-31
LGS1 | Forecast Down Time | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 7598
| Total Operating | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8904
| Actual Plan Outage hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.37 | 7.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21.87 | 0 | 1.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.36 | 16.26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.86
| Standby hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.83 | 0 | 0 | 0 | 14.416 | 1.76 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 18.02 | 1.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.23 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.856
| Force outage by Maintenance | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.53
| Force outage by Operation | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.73 | 24 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.31
| Total Down Time Hours | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 7.37 | 7.42 | 0 | 0 | 0 | 0 | 0 | 0.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.65 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21.87 | 0 | 1.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.73 | 24 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | 24 | 0.35 | 0 | 0 | 2.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.36 | 16.26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.7
| Operating Hours | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.78 | 24 | 24 | 24 | 24 | 24 | 16.63 | 16.58 | 24 | 24 | 24 | 24 | 24 | 23.19 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 9.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 24 | 22.22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 18.2 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 17.63 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 6.27 | 0 | 23.03 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 23.65 | 24 | 24 | 21.18 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.37 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 2.67 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 9.27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 15.64 | 7.74 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.67 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20.93 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.17 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 7524.3
| Physical Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.08% | 100% | 100% | 100% | 100% | 100% | 69.29% | 69.08% | 100% | 100% | 100% | 100% | 100% | 96.62% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 38.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 8.875% | 100% | 92.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 75.83% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 73.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 26.12% | 0% | 95.96% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 98.54% | 100% | 100% | 88.25% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 93.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 11.12% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 38.62% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 65.17% | 32.25% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 87.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.54% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 84.5%
| Utilization of Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 93.42% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.38% | 0% | 0% | 0% | 39.04% | 92.67% | 96.67% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.12% | 100% | 100% | 100% | 100% | 100% | 100% | 99.17% | 24.92% | 60.67% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.75% | 100% | 100% | 100% | 100% | 100% | 97.38% | 99.04% | 98.42% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.43%
| Number of external trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
| Number of internal trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
| Number of Down by Maintenance | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MTBF | Day | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 95.78 | 119.78 | 143.78 | 167.78 | 24 | 48 | 64.63 | 81.21 | 105.21 | 129.21 | 153.21 | 24 | 48 | 71.19 | 95.19 | 119.19 | 143.19 | 167.19 | 24 | 48 | 72 | 96 | 120 | 129.35 | 129.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 26.13 | 48.35 | 72.35 | 96.35 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 162.2 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 137.63 | 161.63 | 24 | 48 | 72 | 96 | 120 | 144 | 75.135 | 0 | 23.03 | 47.03 | 71.03 | 95.03 | 119.03 | 143.03 | 24 | 48 | 72 | 72 | 72 | 72 | 47.825 | 12 | 24 | 34.59 | 46.59 | 58.59 | 70.59 | 82.59 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 166.37 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 146.67 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 129.27 | 153.27 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 87.64 | 95.38 | 95.38 | 95.38 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 22.67 | 46.67 | 70.67 | 94.67 | 118.67 | 142.67 | 166.67 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 140.93 | 164.93 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 95.17 | 119.17 | 143.17 | 167.17 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168
| MTTR | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Note on M7: Asep Mulyana: A1G1 CB was opened - LGS#1 put on standby prepare split to FCE’s Grid, then back in service to supply FCE’s Grid (outage 0.20 hrs) - LGS#1 put on standby prepare split to Auxiliary Grid, then LGS#1 back in service to supply Auxiliary Grid (outage 0.10 hrs)
Note on U9: Asep Mulyana: Hydro to FCE grid black out - BLN 52G1 & 52G2 CB & A3G1 CB was trip - LRN A1G2 & A1G3 CB, A3L4 CB & A3L3 CB, KRB A3G4 & A3G3 CB was trip.
Note on AA6: Asep Mulyana: LGS#1 shutdown for generator protection check, CW-101 replace & Turbine Hira
Note on AB6: Asep Mulyana: LGS#1 shut down for PM Check & HIRA. Ion
Note on AH9: Asep Mulyana: LGS#1 Trip by request from PLC Alarm ( Penstock gate close trip)
Note on AR8: Asep Mulyana: Un-Planned Shutdown LGS#1 SD for check & repair LCB & UGB flow meter was problem & penstock intake gate recycle failure alarm.
Note on AS8: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AT6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AU6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AV6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AW6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AX6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AY6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on AZ6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BA6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BB6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BC6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BD6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BE6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BF6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BG6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BH6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BI6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BJ6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BK6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BL6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BM6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BN6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BO6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BP6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BQ6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BR6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BS6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BT6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BU6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BV6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BW6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BX6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BY6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on BZ6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CA6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CB6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CC6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CD6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CE6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CF6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CG6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CH6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CI6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CJ6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CK6: Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing
Note on CL6: Asep Mulyan LGS#1 Shutdown for Trafo MTX #1 Replacement - commissioning LGS#1 back inservice for supply FCE’s grid
Note on CN6: Asep Mulyana: LGS#1 shut down for connect relay protection 187B (BUS Protection)
Note on DR6: Asep Mulyana: LGS#1 shutdown to standstill for MTX Check & re-torque connection bushing insulator.
Note on EC7: Asep Mulyana: LGS#1 SNL for split to aux grid // KGS#2.
Note on ES8: Asep Mulyana: LGS#1 Unplanned Shudown for Check TGBX vibration sistem.
Note on ET7: Asep Mulyana: LGS#1 put to SNL for prepare split to FCE Grid
Note on FA9: Asep Mulyana: LGS#1 suddenly trip by 86 N realy due to 80TGB relay active.
Note on FB9: Asep Mulyana: LGS#1 suddenly trip by 86 N realy due to 80TGB relay active.
Note on FC9: Asep Mulyana: LGS#1 try auto synconenize to aux grid (can’t syncrone
Note on FK7: Asep Mulyana: LGS#1 turn off for prepare canal SD. Bano RWL: 165.79 Masl, Krb RWL 77.24 Masl
Note on FL6: Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection
Note on FM6: Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection
Note on FN6: Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection
Note on FO7: Asep Mulyana: LGS#1 back to online for supply FCE’s Grid
Note on FO9: Asep Mulyana: LGS#1-2 trip to Standstill - BGS 52-G2, A3G3, A3G4, A3L4 CB & A3L6 CB trip by Breaker Failure from A3G1 CB. - TB
Note on FP7: Asep Mulyana: LGS#1 put in standby for split to Aux
Note on FQ7: Asep Mulyana: Unit Standby
Note on FR8: Asep Mulyana: LGS#1 was shutted off for check & replace CW-117 relief valve
Note on IN8: Asep Mulyana: LGS#1 was shut off to SNL for replace module processor T60.
Note on JG7: Asep Mulyana: - LGS#1 SNL for split to FCE grid (Outage 0.32hrs) - LGS#1 SNL for split to Aux.grid (Outage 0.37hrs)
Note on JN7: Asep Mulyana: LGS#1 back on line to supply FCE grid
Note on JO7: Asep Mulyana: LGS#1 back on line to supply FCE grid
Note on JP7: Asep Mulyana: LGS#1 SNL for split to aux. grid
Note on JP8: Asep Mulyana: LGS#1 Syncronized problem
Note on KJ8: Asep Mulyana: LGS#1 Shutdown pengetesan SPMA syncronizing (put to speed no load for transfer bus.) Problem : - Trouble shoot Breaker CB A1G1 - Auto sync. Several times is failed - Manual Sync - Failed (contact relay temporary pada sync terbakar) - Using existing 2 coil - tripped
Note on KV6: Asep Mulyana: LGS#1 s/down for A1-T1CB assessment
Note on KW6: Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment.
Note on KX6: Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment.
Note on KY6: Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment.
Note on LN9: Asep Mulyana: LGS#1 trip Under Freq (Stn BO)
Note on LX7: Asep Mulyana: LGS#1 was shut off to SNL for split to Aux.grid
Note on MD7: Asep Mulyana: LGS#1 was shut off to SNL for PMC Disc Switch in Bus#A-21.
Note on ME7: Asep Mulyana: LGS#2 was shut off to SNL for split to FCE’s grid (purpose for PMC Disc Switch in Thermal Bus#A-21)
Note on MF7: Asep Mulyana: LGS#2 was shut off to SNL for split to FCE’s grid (purpose for PMC Disc Switch in Thermal Bus#A-21)
Note on MG9: Asep Mulyana: Tripped by TBO LGS#1 A1G1 Trip to SNL, BGS#1-2 Trip to Turbine Operation, KGS#1 Trip to Turbine Operation and KGS#2 Turbine Operation ( KGS#2 under Test Function Test).
Note on MS9: Asep Mulyana: FCE grid BO. A1-G1, A1-G2, A1-G3, A1L1, A1L2, A3L3, KGS 52-G1 CB trip. Note: - LGS#1 trip to standstill by 86E & 86N. - LGS#2 trip to Speed No Load. - LGS#3 trip to standstill by 86E & 86N. - KGS#1 trip to Turbine Operation by Non Lockout 94.

## PA_Power_Summary
Date | Planned Down Time (Hour) | Total Operating (Hour) | Actual Plan Outage hrs (Hour) | Standby hrs (Hour) | Force outage by Maintenance (Hour) | Force outage by Operation (Hour) | Total Down Time Hours (Hour) | Operating Hours (Hour) | Physical Availability (%) | Utilization of Availability (%) | Number of external trip/failure (Times) | Number of internal trip/failure (Times) | Number of Down by Maintenance (Times) | MTBF (Day) | MTTR (Hour) | Remarks | Category | LGS Status | Activity or Problem | Related Component | Note
2021-01-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-01-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-01-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-01-04 | 24 | 24 | 0 | 0.3 | 0 | 0 | 0 | 24 | 100% | 98.75% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: A1G1 CB was opened - LGS#1 put on standby prepare split to FCE’s Grid, then back in service to supply FCE’s Grid (outage 0.20 hrs) - LGS#1 put on standby prepare split to Auxiliary Grid, then LGS#1 back in service to supply Auxiliary Grid (outage 0.10 hrs) | Standby | Put on Standby | Prepare Split to Grid | FCE Grid; Auxiliary Grid | Prepare Split to FCE Grid; Prepare Split to Auxiliary Grid
2021-01-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-01-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-01-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-01-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-01-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-01-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-01-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-01-12 | 24 | 24 | 0 | 0 | 0 | 0.22 | 0.22 | 23.78 | 99.08% | 100% | 1 | 0 | 0 | 95.78 | 0 | Asep Mulyana: Hydro to FCE grid black out - BLN 52G1 & 52G2 CB & A3G1 CB was trip - LRN A1G2 & A1G3 CB, A3L4 CB & A3L3 CB, KRB A3G4 & A3G3 CB was trip. | Operation | Hydro to Grid Blackout | Grid Blackout | FCE Grid
2021-01-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.78 | 0 | No outages (Normal operation).
2021-01-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.78 | 0 | No outages (Normal operation).
2021-01-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.78 | 0 | No outages (Normal operation).
2021-01-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-01-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-01-18 | 0 | 24 | 7.37 | 0 | 0 | 0 | 7.37 | 16.63 | 69.29% | 100% | 0 | 0 | 0 | 64.63 | 0 | Asep Mulyana: LGS#1 shutdown for generator protection check, CW-101 replace & Turbine Hira | Actual Plant Outage | Shutdown | Protection Check; Component Replace; HIRA | Generator; CW-101; Turbine
2021-01-19 | 0 | 24 | 7.42 | 0 | 0 | 0 | 7.42 | 16.58 | 69.08% | 100% | 0 | 0 | 0 | 81.21 | 0 | Asep Mulyana: LGS#1 shut down for PM Check & HIRA. Ion | Actual Plant Outage | Shutdown | PM Check; HIRA | LGS; Ion
2021-01-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 105.21 | 0 | No outages (Normal operation).
2021-01-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 129.21 | 0 | No outages (Normal operation).
2021-01-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 153.21 | 0 | No outages (Normal operation).
2021-01-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-01-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-01-25 | 24 | 24 | 0 | 0 | 0 | 0.81 | 0.81 | 23.19 | 96.62% | 100% | 1 | 0 | 0 | 71.19 | 0 | Asep Mulyana: LGS#1 Trip by request from PLC Alarm ( Penstock gate close trip) | Operation | Trip | Request from PLC Alarm | Penstock Gate | Penstock Gate Close Trip
2021-01-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.19 | 0 | No outages (Normal operation).
2021-01-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.19 | 0 | No outages (Normal operation).
2021-01-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.19 | 0 | No outages (Normal operation).
2021-01-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.19 | 0 | No outages (Normal operation).
2021-01-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-01-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-02-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-02-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-02-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-02-04 | 24 | 24 | 0 | 0 | 14.65 | 0 | 14.65 | 9.35 | 38.96% | 100% | 0 | 0 | 0 | 129.35 | 0 | Asep Mulyana: Un-Planned Shutdown LGS#1 SD for check & repair LCB & UGB flow meter was problem & penstock intake gate recycle failure alarm. | Maintenance | Shutdown | Check and Repair | LGB; UGB; Penstock | Bearing Flow Meter problem; Penstock Intake Gain Alarm
2021-02-05 | 24 | 24 | 0 | 0 | 24 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 129.35 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Maintenance | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-06 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-07 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-08 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-09 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-10 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-11 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-12 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-13 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-14 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-15 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-16 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-17 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-18 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-19 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-20 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-21 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-22 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-23 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-24 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-25 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-26 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-27 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-02-28 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-01 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-02 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-03 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-04 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-05 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-06 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-07 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-08 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-09 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-10 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-11 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-12 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-13 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-14 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-15 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-16 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-17 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-18 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-19 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-20 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-21 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyan LGS#1 Shutdown for Repair Trafo MTX #1 Widing | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-22 | 0 | 24 | 21.87 | 0 | 0 | 0 | 21.87 | 2.13 | 8.875% | 100% | 0 | 0 | 0 | 2.13 | 0 | Asep Mulyan LGS#1 Shutdown for Trafo MTX #1 Replacement - commissioning LGS#1 back inservice for supply FCE’s grid | Actual Plant Outage | Shutdown | Repair Component | Trafo MTX#1 Widing
2021-03-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 26.13 | 0 | No outages (Normal operation).
2021-03-24 | 22 | 24 | 1.78 | 0 | 0 | 0 | 1.78 | 22.22 | 92.58% | 100% | 0 | 0 | 0 | 48.35 | 0 | Asep Mulyana: LGS#1 shut down for connect relay protection 187B (BUS Protection) | Actual Plant Outage | Shutdown | Connect Protection | Relay Protection 187B (Bus Protection)
2021-03-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72.35 | 0 | No outages (Normal operation).
2021-03-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96.35 | 0 | No outages (Normal operation).
2021-03-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-03-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-03-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-03-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-03-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-04-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-04-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-04-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-04-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-04-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-04-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-04-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-04-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-04-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-04-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-04-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-04-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-04-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-04-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-04-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-04-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-04-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-04-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-04-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-04-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-04-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-04-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-04-23 | 16 | 24 | 5.8 | 0 | 0 | 0 | 5.8 | 18.2 | 75.83% | 100% | 0 | 0 | 0 | 162.2 | 0 | Asep Mulyana: LGS#1 shutdown to standstill for MTX Check & re-torque connection bushing insulator. | Actual Plant Outage | Shutdown to Standstill | Check and Repair | MTX; Re-torque connection bushing insulator
2021-04-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-04-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-04-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-04-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-04-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-04-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-04-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-05-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-05-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-05-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-05-04 | 24 | 24 | 0 | 1.58 | 0 | 0 | 0 | 24 | 100% | 93.42% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 SNL for split to aux grid // KGS#2. | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2021-05-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-05-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-05-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-05-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-05-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-05-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-05-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-05-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-05-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-05-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-05-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-05-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-05-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-05-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-05-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-05-20 | 24 | 24 | 0 | 0 | 6.37 | 0 | 6.37 | 17.63 | 73.46% | 100% | 0 | 0 | 0 | 137.63 | 0 | Asep Mulyana: LGS#1 Unplanned Shudown for Check TGBX vibration sistem. | Maintenance | Shutdown (Unplanned) | Component Check | TGBX Vibration System
2021-05-21 | 24 | 24 | 0 | 0.67 | 0 | 0 | 0 | 24 | 100% | 97.21% | 0 | 0 | 0 | 161.63 | 0 | Asep Mulyana: LGS#1 put to SNL for prepare split to FCE Grid | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2021-05-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-05-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-05-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-05-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-05-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-05-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-05-28 | 24 | 24 | 0 | 0 | 0 | 17.73 | 17.73 | 6.27 | 26.12% | 100% | 0 | 1 | 0 | 75.135 | 0 | Asep Mulyana: LGS#1 suddenly trip by 86 N realy due to 80TGB relay active. | Operation | Suddenly Trip | Relay Active | 80TGB Relay Active
2021-05-29 | 24 | 24 | 0 | 0 | 0 | 24 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 0 | 0 | Asep Mulyana: LGS#1 suddenly trip by 86 N realy due to 80TGB relay active. | Operation | Suddenly Trip | Relay Active | 80TGB Relay Active
2021-05-30 | 24 | 24 | 0 | 0 | 0 | 0.97 | 0.97 | 23.03 | 95.96% | 100% | 0 | 0 | 0 | 23.03 | 0 | Asep Mulyana: LGS#1 try auto synconenize to aux grid (can’t syncrone | Operation | Try Synchronize to Grid | Can’t Synchronize | Auxiliary Grid
2021-05-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 47.03 | 0 | No outages (Normal operation).
2021-06-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 71.03 | 0 | No outages (Normal operation).
2021-06-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.03 | 0 | No outages (Normal operation).
2021-06-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.03 | 0 | No outages (Normal operation).
2021-06-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.03 | 0 | No outages (Normal operation).
2021-06-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-06-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-06-07 | 24 | 24 | 0 | 1.83 | 0 | 0 | 0 | 24 | 100% | 92.38% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 turn off for prepare canal SD. Bano RWL: 165.79 Masl, Krb RWL 77.24 Masl | Standby | Turn off | Component Check | Canal | Canal Shutdown/Inspection
2021-06-08 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection | Actual Plant Outage | Shutdown | Component Check | Canal | Canal Shutdown/Inspection
2021-06-09 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection | Actual Plant Outage | Shutdown | Component Check | Canal | Canal Shutdown/Inspection
2021-06-10 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#2 shutted down for canal shut down/Inspection | Actual Plant Outage | Shutdown | Component Check | Canal | Canal Shutdown/Inspection
2021-06-11 | 24 | 24 | 0 | 14.416 | 0 | 0.35 | 0.35 | 23.65 | 98.54% | 39.04% | 0 | 1 | 0 | 47.825 | 0 | Asep Mulyana: LGS#1 back to online for supply FCE’s Grid Asep Mulyana: LGS#1-2 trip to Standstill - BGS 52-G2, A3G3, A3G4, A3L4 CB & A3L6 CB trip by Breaker Failure from A3G1 CB. - TB | Standby | Back to Online | Supply to Grid | FCE Grid
2021-06-12 | 24 | 24 | 0 | 1.76 | 0 | 0 | 0 | 24 | 100% | 92.67% | 0 | 1 | 0 | 12 | 0 | Asep Mulyana: LGS#1 put in standby for split to Aux | Standby | Put on Standby | Prepare Split to Grid | Auxiliary Grid
2021-06-13 | 24 | 24 | 0 | 0.8 | 0 | 0 | 0 | 24 | 100% | 96.67% | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: Unit Standby | Standby | Put on Standby | Unit/Component Standby | Unit Standby
2021-06-14 | 24 | 24 | 0 | 0 | 2.82 | 0 | 2.82 | 21.18 | 88.25% | 100% | 0 | 0 | 0 | 34.59 | 0 | Asep Mulyana: LGS#1 was shutted off for check & replace CW-117 relief valve | Maintenance | Shutted off | Check and Repair | CW-117 Relief Valve
2021-06-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 46.59 | 0 | No outages (Normal operation).
2021-06-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 58.59 | 0 | No outages (Normal operation).
2021-06-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 70.59 | 0 | No outages (Normal operation).
2021-06-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 82.59 | 0 | No outages (Normal operation).
2021-06-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-06-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-06-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-06-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-06-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-06-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-06-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-06-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-06-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-06-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-06-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-06-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-07-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-07-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-07-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-07-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-07-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-07-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-07-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-07-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-07-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-07-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-07-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-07-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-07-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-07-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-07-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-07-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-07-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-07-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-07-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-07-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-07-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-07-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-07-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-07-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-07-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-07-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-07-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-07-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-07-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-07-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-07-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-08-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-08-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-08-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-08-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-08-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-08-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-08-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-08-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-08-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-08-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-08-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-08-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-08-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-08-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-08-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-08-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-08-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-08-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-08-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-08-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-08-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-08-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-08-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-08-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-08-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-08-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-08-27 | 24 | 24 | 0 | 0 | 1.63 | 0 | 1.63 | 22.37 | 93.21% | 100% | 0 | 0 | 0 | 166.37 | 0 | Asep Mulyana: LGS#1 was shut off to SNL for replace module processor T60. | Standby | Speed No Load | Repair Component | Modul Processor T60
2021-08-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-08-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-08-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-08-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-09-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-09-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-09-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-09-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-09-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-09-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-09-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-09-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-09-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-09-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-09-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-09-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-09-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-09-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-09-15 | 24 | 24 | 0 | 0.69 | 0 | 0 | 0 | 24 | 100% | 97.12% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: - LGS#1 SNL for split to FCE grid (Outage 0.32hrs) - LGS#1 SNL for split to Aux.grid (Outage 0.37hrs) | Standby | Speed No Load | Prepare Split to Grid | FCE Grid; Auxiliary Grid
2021-09-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-09-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-09-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-09-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-09-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-09-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-09-22 | 24 | 24 | 0 | 0.2 | 0 | 0 | 0 | 24 | 100% | 99.17% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#1 back on line to supply FCE grid | Standby | Back to Online | Supply to Grid | FCE Grid
2021-09-23 | 24 | 24 | 0 | 18.02 | 0 | 0 | 0 | 24 | 100% | 24.92% | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: LGS#1 back on line to supply FCE grid | Standby | Back to Online | Supply to Grid | FCE Grid
2021-09-24 | 24 | 24 | 0 | 1.05 | 21.33 | 0 | 21.33 | 2.67 | 11.12% | 60.67% | 0 | 0 | 0 | 146.67 | 0 | Asep Mulyana: LGS#1 SNL for split to aux. grid Asep Mulyana: LGS#1 Syncronized problem | Standby, Maintenance | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2021-09-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-09-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-09-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-09-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-09-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-09-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-10-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-10-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-10-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-10-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-10-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-10-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-10-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-10-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-10-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-10-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-10-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-10-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-10-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-10-14 | 24 | 24 | 0 | 0 | 14.73 | 0 | 14.73 | 9.27 | 38.62% | 100% | 0 | 0 | 0 | 129.27 | 0 | Asep Mulyana: LGS#1 Shutdown pengetesan SPMA syncronizing (put to speed no load for transfer bus.) Problem : - Trouble shoot Breaker CB A1G1 - Auto sync. Several times is failed - Manual Sync - Failed (contact relay temporary pada sync terbakar) - Using existing 2 coil - tripped | Maintenance | Speed No Load | Transfer Bus | Bus System
2021-10-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 153.27 | 0 | No outages (Normal operation).
2021-10-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-10-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-10-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-10-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-10-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-10-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-10-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-10-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-10-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-10-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-10-26 | 0 | 24 | 8.36 | 0 | 0 | 0 | 8.36 | 15.64 | 65.17% | 100% | 0 | 0 | 0 | 87.64 | 0 | Asep Mulyana: LGS#1 s/down for A1-T1CB assessment | Actual Plant Outage | Shutdown | Component Check | A1-T1CB Assessment
2021-10-27 | 0 | 24 | 16.26 | 0 | 0 | 0 | 16.26 | 7.74 | 32.25% | 100% | 0 | 0 | 0 | 95.38 | 0 | Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment. | Actual Plant Outage | Shutdown | Component Check | A1-T1CB Assessment
2021-10-28 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 95.38 | 0 | Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment. | Actual Plant Outage | Shutdown | Component Check | A1-T1CB Assessment
2021-10-29 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 95.38 | 0 | Asep Mulyana: LGS#1 s/down for continue A1-T1CB assessment. | Actual Plant Outage | Shutdown | Component Check | A1-T1CB Assessment
2021-10-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-10-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-11-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-11-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-11-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-11-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-11-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-11-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-11-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-11-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-11-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-11-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-11-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-11-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-11-13 | 24 | 24 | 0 | 0 | 0 | 1.33 | 1.33 | 22.67 | 94.46% | 100% | 1 | 0 | 0 | 22.67 | 0 | Asep Mulyana: LGS#1 trip Under Freq (Stn BO) | Operation | Trip | Under Frequency (Stn BO) | LGS
2021-11-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 46.67 | 0 | No outages (Normal operation).
2021-11-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 70.67 | 0 | No outages (Normal operation).
2021-11-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 94.67 | 0 | No outages (Normal operation).
2021-11-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 118.67 | 0 | No outages (Normal operation).
2021-11-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 142.67 | 0 | No outages (Normal operation).
2021-11-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 166.67 | 0 | No outages (Normal operation).
2021-11-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-11-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-11-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-11-23 | 24 | 24 | 0 | 0.3 | 0 | 0 | 0 | 24 | 100% | 98.75% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 was shut off to SNL for split to Aux.grid | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2021-11-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-11-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-11-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-11-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-11-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-11-29 | 24 | 24 | 0 | 0.63 | 0 | 0 | 0 | 24 | 100% | 97.38% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 was shut off to SNL for PMC Disc Switch in Bus#A-21. | Standby | Speed No Load | PMC Disc Switch | Bus#A-21
2021-11-30 | 24 | 24 | 0 | 0.23 | 0 | 0 | 0 | 24 | 100% | 99.04% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#2 was shut off to SNL for split to FCE’s grid (purpose for PMC Disc Switch in Thermal Bus#A-21) | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2021-12-01 | 24 | 24 | 0 | 0.38 | 0 | 0 | 0 | 24 | 100% | 98.42% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#2 was shut off to SNL for split to FCE’s grid (purpose for PMC Disc Switch in Thermal Bus#A-21) | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2021-12-02 | 24 | 24 | 0 | 0 | 0 | 3.07 | 3.07 | 20.93 | 87.21% | 100% | 1 | 0 | 0 | 140.93 | 0 | Asep Mulyana: Tripped by TBO LGS#1 A1G1 Trip to SNL, BGS#1-2 Trip to Turbine Operation, KGS#1 Trip to Turbine Operation and KGS#2 Turbine Operation ( KGS#2 under Test Function Test). | Operation | Trip | Total Black Out | A1G1
2021-12-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 164.93 | 0 | No outages (Normal operation).
2021-12-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-12-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-12-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-12-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-12-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-12-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-12-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-12-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-12-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-12-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-12-14 | 24 | 24 | 0 | 0 | 0 | 0.83 | 0.83 | 23.17 | 96.54% | 100% | 1 | 0 | 0 | 95.17 | 0 | Asep Mulyana: FCE grid BO. A1-G1, A1-G2, A1-G3, A1L1, A1L2, A3L3, KGS 52-G1 CB trip. Note: - LGS#1 trip to standstill by 86E & 86N. - LGS#2 trip to Speed No Load. - LGS#3 trip to standstill by 86E & 86N. - KGS#1 trip to Turbine Operation by Non Lockout 94. | Operation | Trip | Grid Blackout | FCE Grid
2021-12-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.17 | 0 | No outages (Normal operation).
2021-12-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.17 | 0 | No outages (Normal operation).
2021-12-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.17 | 0 | No outages (Normal operation).
2021-12-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-12-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-12-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-12-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-12-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-12-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-12-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2021-12-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2021-12-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2021-12-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2021-12-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2021-12-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2021-12-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2021-12-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).