## PA_Power_Data
| Unit | Week #1 | [6 empty] | Week #2 | [6 empty] | Week #3 | [6 empty] | Week #4 | [6 empty] | Week #5 | [6 empty] | Week #6 | [6 empty] | Week #7 | [6 empty] | Week #8 | [6 empty] | Week #9 | [6 empty] | Week #10 | [6 empty] | Week #11 | [6 empty] | Week #12 | [6 empty] | Week #13 | [6 empty] | Week #14 | [6 empty] | Week #15 | [6 empty] | Week #16 | [6 empty] | Week #17 | [6 empty] | Week #18 | [6 empty] | Week #19 | [6 empty] | Week #20 | [6 empty] | Week #21 | [6 empty] | Week #22 | [6 empty] | Week #23 | [6 empty] | Week #24 | [6 empty] | Week #25 | [6 empty] | Week #26 | [6 empty] | Week #27 | [6 empty] | Week #28 | [6 empty] | Week #29 | [6 empty] | Week #30 | [6 empty] | Week #31 | [6 empty] | Week #32 | [6 empty] | Week #33 | [6 empty] | Week #34 | [6 empty] | Week #35 | [6 empty] | Week #36 | [6 empty] | Week #37 | [6 empty] | Week #38 | [6 empty] | Week #39 | [6 empty] | Week #40 | [6 empty] | Week #41 | [6 empty] | Week #42 | [6 empty] | Week #43 | [6 empty] | Week #44 | [6 empty] | Week #45 | [6 empty] | Week #46 | [6 empty] | Week #47 | [6 empty] | Week #48 | [6 empty] | Week #49 | [6 empty] | Week #50 | [6 empty] | Week #51 | [6 empty] | Week #52 | [6 empty] | 1
2 | time axis 2022-12-31 to 2023-12-29
3
Planned Down Time | Hour | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 1 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 8 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 8 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 4 | 5.3333
Total Operating | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 5
Actual Plan Outage hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
Standby hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.08 | 0 | 0 | 0.63 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0.18 | 0.1 | 0.23 | 0 | 0.11 | 0.45 | 0 | 0 | 0 | 0 | 0.15 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
Force outage by Maintenance | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
Force outage by Operation | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
Total Down Time Hours | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 0 | 0 | 0.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 2.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
Operating Hours | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.55 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.67 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.87 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21.8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21.92 | 24 | 24 | 23.42 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.68 | 24 | 24 | 24 | 24 | 24 | 24 | 21.62 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20.6 | 24 | 24 | 24 | 24 | 24 | 24 | 16.65 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.83 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.67 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.72 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 11
Physical Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 93.96% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.62% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90.83% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 91.33% | 100% | 100% | 97.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.67% | 100% | 100% | 100% | 100% | 100% | 100% | 90.08% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 85.83% | 100% | 100% | 100% | 100% | 100% | 100% | 69.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.29% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.83% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 12
Utilization of Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.79% | 100% | 100% | 100% | 100% | 100% | 100% | 99.71% | 99.67% | 100% | 100% | 97.38% | 100% | 100% | 100% | 99.38% | 100% | 100% | 99.25% | 99.58% | 99.04% | 100% | 99.54% | 98.12% | 100% | 100% | 100% | 100% | 99.38% | 99.17% | 99.17% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 95.29% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.71% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.88% | 100% | 100% | 100% | 100% | 100% | 98.96% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 100% | 99.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.79% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 13
Number of external trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14
Number of internal trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15
Number of Down by Maintenance | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
MTBF | Day | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 46.55 | 70.55 | 94.55 | 118.55 | 142.55 | 166.55 | 24 | 48 | 71.67 | 95.67 | 119.67 | 143.67 | 167.67 | 24 | 48 | 72 | 96 | 120 | 144 | 167.87 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 141.8 | 165.8 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 165.92 | 24 | 48 | 35.71 | 47.71 | 59.71 | 71.71 | 83.71 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 35.84 | 47.84 | 59.84 | 71.84 | 83.84 | 24 | 48 | 69.62 | 93.62 | 117.62 | 141.62 | 165.62 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 140.6 | 164.6 | 24 | 48 | 72 | 96 | 120 | 136.65 | 160.65 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 71.83 | 95.83 | 119.83 | 143.83 | 167.83 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 22.67 | 46.67 | 70.67 | 94.67 | 118.67 | 142.67 | 166.67 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 119.72 | 143.72 | 167.72 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 17
MTTR | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18
|  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Note on L7: Asep Mulyana: put standby for split to FCE grid
Note on Q4: Asep Mulyana: PM Check Yearly
Note on R4: Asep Mulyana: PM Check Yearly
Note on S4: Asep Mulyana: PM Check Yearly
Note on S7: Asep Mulyana: LGS#1 put on standby due to prepare split to Auxiliary grid.
Note on T4: Asep Mulyana: PM Check Yearly
Note on T7: Asep Mulyana: LGS#1 split to FCE grid
Note on U4: Asep Mulyana: PM Check Yearly
Note on V4: Asep Mulyana: PM Check Yearly
Note on W4: Asep Mulyana: PM Check Yearly
Note on W7: Asep Mulyana: LGS#1 put to SNL prepare split to Aux grid
Note on AA7: Asep Mulyana: LGS#1 prepare split to FCE grid
Note on AD7: Asep Mulyana: LGS#1 back online and ready to supply FCE grid outage 0.15 hrs - LGS#1 back online and ready to supply Aux grid outage 0.03 hrs
Note on AE7: Asep Mulyana: LGS#1 prepare split to FCE grid (0.03 hrs) - LGS#1 back online and ready to supply Aux grid. (0.07 hrs)
Note on AF7: Asep Mulyana: - LGS#1 prepare split to FCE grid. - LGS#1 prepare split to Aux grid
Note on AH7: Asep Mulyana: LGS#1 prepare split to FCE grid - LGS#1 SNL for split to aux grid
Note on AI7: Asep Mulyana: LGS#1 prepare split to FCE grid - LGS#1 for prepare split to Aux grid
Note on AN7: Asep Mulyana: LGS#1 SNL for split to FCE grid. - LGS#1 SNL for split to aux grid
Note on AO7: Asep Mulyana: - LGS#1 SNL for split to FCE grid. - LGS#1 SNL for split to Aux grid
Note on AP7: Asep Mulyana: - LGS#1 SNL for split to FCE grid - LGS#1 SNL for split to Aux grid
Note on BA9: Asep Mulyana: Total Black Out occurred due to LRN A1L1 CB trip (Line aux trip) & Suspected fault came from signal cam switch A1L12 DS 100. (A1L1 CB, A1-G1 CB, A1-G2 CB, A1-G3 CB, A3G1 CB, A3G2 CB, A3T1 CB, BGS 52-G1 CB, BGS 52-G2 CB, KGS 52-G1 CB & KGS 52-G2 CB were opened).
Note on BI9: Asep Mulyana: Furnace grid BO - Load shedding active A1L1 CB, A1L2 CB, A1-G1 CB, A1-G2 CB, A1-G3 CB, A3G1 CB, A3G2 CB, BGS 52-G1 CB, BGS 52-G2 CB & KGS 52-G1 CB was open
Note on BT9: Asep Mulyana: TBO occurred, A1G1 CB, A1G2 CB, A1G3 CB, BLB 52G1 CB, BLB 52G2 CB, BLB A3G1 CB, BLB A3G2 CB, KRB 52G1 CB, KRB 52G2 CB & LRN A1L1 CB was trip.
Note on BX7: Asep Mulyana: LGS#1 put to speed No load for prepare split to FCE grid 0.48 hrs - LGS#1 back online & supply aux grid. Outage = 0.65 hrs.
Note on CG8: Asep Mulyana: LGS#1 shut down for check & repair hydrant PPM MTX.
Note on DJ6: Asep Mulyana: LGS#1 shutdown for replace 10 ea carbon brush
Note on DM9: Asep Mulyana: LGS#1 tripp by 186 TX hand reset lockout relay & 86 emergency shutdown trip operated
Note on EO9: Asep Mulyana: LGS#1 trip by 86N relay energized (TGB Oil level low alarm trip)
Note on EV8: Asep Mulyana: LGS#1 shutdown for check floating switch & TGB oil level sensor.
Note on GO8: Asep Mulyana: LGS#1 shut down for investigation trip.
Note on GV6: Asep Mulyana: LGS#1 shut down 8 hrs for PMO HIRA & General PM Check.
Note on GZ7: Asep Mulyana: - LGS#1 split to aux grid, and back OL supply aux grid. Outage = 0.05 hrs. - LGS#1 split to FCE grid, and back OL supply FCE grid. Outage = 0.02 hrs.
Note on HG9: Asep Mulyana: Furnace BO occurred, A1G1 CB, Bano 52G1, Bano 52G2, KRB 52G1 CB was trip to Turbine operation by Under Frequency & LGS#1 was trip by over Excitacy.
Note on IC7: Asep Mulyana: LGS#1 SNL for split to aux via line#1 // KGS#2
Note on II7: Asep Mulyana: LGS#1 stand by SNL for split to FCE Grid
Note on IN7: Asep Mulyana: LGS#1 put to speed No Load for split to Aux grid
Note on IR7: Asep Mulyana: LGS#1 split to FCE grid
Note on IZ7: Asep Mulyana: LGS#1 split to Bus A12.
Note on JB9: Asep Mulyana: Furnace BO occurred, A1G1 CB, A1G3 CB, A3G1 CB, A3G2 CB, Bano 52G1, Bano 52G2, KRB 52G1 CB was trip to Turbine operation.BGS#1-2, KGS#1, LGS#1-3 trip by Over Frequency.
Note on JT9: Asep Mulyana: FCE Grid Blackout

## PA_Power_Summary
Date | Planned Down Time (Hour) | Total Operating (Hour) | Actual Plan Outage hrs (Hour) | Standby hrs (Hour) | Force outage by Maintenance (Hour) | Force outage by Operation (Hour) | Total Down Time Hours (Hour) | Operating Hours (Hour) | Physical Availability (%) | Utilization of Availability (%) | Number of external trip/failure (Times) | Number of internal trip/failure (Times) | Number of Down by Maintenance (Times) | MTBF (Day) | MTTR (Hour) | Remarks | Category | LGS Status | Activity or Problem | Related Component | Note
2022-12-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-01-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-01-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-01-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-01-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-01-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-01-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-01-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-01-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-01-09 | 0.48 | 24 | 0 | 0.05 | 0 | 0 | 0 | 24 | 100% | 99.79% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: put standby for split to FCE grid
2023-01-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-01-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-01-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-01-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-01-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: PM Check Yearly
2023-01-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | Asep Mulyana: PM Check Yearly
2023-01-16 | 24 | 24 | 0 | 0.07 | 0 | 0 | 0 | 24 | 100% | 99.71% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: PM Check Yearly Asep Mulyana: LGS#1 put on standby due to prepare split to Auxiliary grid.
2023-01-17 | 24 | 24 | 0 | 0.08 | 0 | 0 | 0 | 24 | 100% | 99.67% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: PM Check Yearly Asep Mulyana: LGS#1 split to FCE grid
2023-01-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: PM Check Yearly
2023-01-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: PM Check Yearly
2023-01-20 | 24 | 24 | 0 | 0.63 | 0 | 0 | 0 | 24 | 100% | 97.38% | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: PM Check Yearly Asep Mulyana: LGS#1 put to SNL prepare split to Aux grid
2023-01-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-01-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-01-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-01-24 | 0.48 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 100% | 99.38% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 prepare split to FCE grid
2023-01-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-01-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-01-27 | 0.48 | 24 | 0 | 0.18 | 0 | 0 | 0 | 24 | 100% | 99.25% | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: LGS#1 back online and ready to supply FCE grid outage 0.15 hrs - LGS#1 back online and ready to supply Aux grid outage 0.03 hrs
2023-01-28 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 100% | 99.58% | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 prepare split to FCE grid (0.03 hrs) - LGS#1 back online and ready to supply Aux grid. (0.07 hrs)
2023-01-29 | 0.48 | 24 | 0 | 0.23 | 0 | 0 | 0 | 24 | 100% | 99.04% | 0 | 0 | 0 | 48 | 0 | Asep Mulyana: - LGS#1 prepare split to FCE grid. - LGS#1 prepare split to Aux grid
2023-01-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-01-31 | 0.48 | 24 | 0 | 0.11 | 0 | 0 | 0 | 24 | 100% | 99.54% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 prepare split to FCE grid - LGS#1 SNL for split to aux grid
2023-02-01 | 0.48 | 24 | 0 | 0.45 | 0 | 0 | 0 | 24 | 100% | 98.12% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#1 prepare split to FCE grid - LGS#1 for prepare split to Aux grid
2023-02-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-02-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-02-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-02-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-02-06 | 0.48 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 100% | 99.38% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 SNL for split to FCE grid. - LGS#1 SNL for split to aux grid
2023-02-07 | 0.48 | 24 | 0 | 0.2 | 0 | 0 | 0 | 24 | 100% | 99.17% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: - LGS#1 SNL for split to FCE grid. - LGS#1 SNL for split to Aux grid
2023-02-08 | 0.48 | 24 | 0 | 0.2 | 0 | 0 | 0 | 24 | 100% | 99.17% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: - LGS#1 SNL for split to FCE grid - LGS#1 SNL for split to Aux grid
2023-02-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-02-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-02-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-02-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-02-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-02-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-02-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-02-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-02-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-02-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-02-19 | 0.48 | 24 | 0 | 0 | 0 | 1.45 | 1.45 | 22.55 | 93.96% | 100% | 0 | 0 | 0 | 46.55 | 0 | Asep Mulyana: Total Black Out occurred due to LRN A1L1 CB trip (Line aux trip) & Suspected fault came from signal cam switch A1L12 DS 100. (A1L1 CB, A1-G1 CB, A1-G2 CB, A1-G3 CB, A3G1 CB, A3G2 CB, A3T1 CB, BGS 52-G1 CB, BGS 52-G2 CB, KGS 52-G1 CB & KGS 52-G2 CB were opened).
2023-02-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 70.55 | 0 | No outages (Normal operation).
2023-02-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 94.55 | 0 | No outages (Normal operation).
2023-02-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 118.55 | 0 | No outages (Normal operation).
2023-02-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 142.55 | 0 | No outages (Normal operation).
2023-02-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 166.55 | 0 | No outages (Normal operation).
2023-02-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-02-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-02-27 | 0.48 | 24 | 0 | 0 | 0 | 0.33 | 0.33 | 23.67 | 98.62% | 100% | 1 | 0 | 0 | 71.67 | 0 | Asep Mulyana: Furnace grid BO - Load shedding active A1L1 CB, A1L2 CB, A1-G1 CB, A1-G2 CB, A1-G3 CB, A3G1 CB, A3G2 CB, BGS 52-G1 CB, BGS 52-G2 CB & KGS 52-G1 CB was open
2023-02-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.67 | 0 | No outages (Normal operation).
2023-03-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.67 | 0 | No outages (Normal operation).
2023-03-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.67 | 0 | No outages (Normal operation).
2023-03-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.67 | 0 | No outages (Normal operation).
2023-03-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-03-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-03-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-03-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-03-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-03-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-03-10 | 0.48 | 24 | 0 | 0 | 0 | 0.13 | 0.13 | 23.87 | 99.46% | 100% | 0 | 0 | 0 | 167.87 | 0 | Asep Mulyana: TBO occurred, A1G1 CB, A1G2 CB, A1G3 CB, BLB 52G1 CB, BLB 52G2 CB, BLB A3G1 CB, BLB A3G2 CB, KRB 52G1 CB, KRB 52G2 CB & LRN A1L1 CB was trip.
2023-03-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-03-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-03-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-03-14 | 0.48 | 24 | 0 | 1.13 | 0 | 0 | 0 | 24 | 100% | 95.29% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 put to speed No load for prepare split to FCE grid 0.48 hrs - LGS#1 back online & supply aux grid. Outage = 0.65 hrs.
2023-03-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-03-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-03-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-03-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-03-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-03-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-03-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-03-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-03-23 | 0.48 | 24 | 0 | 0 | 2.2 | 0 | 2.2 | 21.8 | 90.83% | 100% | 0 | 0 | 0 | 141.8 | 0 | Asep Mulyana: LGS#1 shut down for check & repair hydrant PPM MTX.
2023-03-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 165.8 | 0 | No outages (Normal operation).
2023-03-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-03-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-03-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-03-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-03-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-03-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-03-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-04-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-04-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-04-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-04-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-04-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-04-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-04-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-04-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-04-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-04-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-04-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-04-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-04-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-04-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-04-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-04-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-04-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-04-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-04-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-04-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-04-21 | 1 | 24 | 2.08 | 0 | 0 | 0 | 2.08 | 21.92 | 91.33% | 100% | 0 | 0 | 0 | 165.92 | 0 | Asep Mulyana: LGS#1 shutdown for replace 10 ea carbon brush
2023-04-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-04-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-04-24 | 0.48 | 24 | 0 | 0 | 0 | 0.58 | 0.58 | 23.42 | 97.58% | 100% | 0 | 1 | 0 | 35.71 | 0 | Asep Mulyana: LGS#1 tripp by 186 TX hand reset lockout relay & 86 emergency shutdown trip operated
2023-04-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 47.71 | 0 | No outages (Normal operation).
2023-04-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 59.71 | 0 | No outages (Normal operation).
2023-04-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 71.71 | 0 | No outages (Normal operation).
2023-04-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 83.71 | 0 | No outages (Normal operation).
2023-04-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-04-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-05-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-05-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-05-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-05-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-05-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-05-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-05-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-05-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-05-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-05-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-05-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-05-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-05-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-05-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-05-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-05-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-05-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-05-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-05-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-05-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-05-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-05-22 | 0.48 | 24 | 0 | 0 | 0 | 0.32 | 0.32 | 23.68 | 98.67% | 100% | 0 | 1 | 0 | 35.84 | 0 | Asep Mulyana: LGS#1 trip by 86N relay energized (TGB Oil level low alarm trip)
2023-05-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 47.84 | 0 | No outages (Normal operation).
2023-05-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 59.84 | 0 | No outages (Normal operation).
2023-05-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 71.84 | 0 | No outages (Normal operation).
2023-05-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 83.84 | 0 | No outages (Normal operation).
2023-05-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-05-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-05-29 | 0.48 | 24 | 0 | 0 | 2.38 | 0 | 2.38 | 21.62 | 90.08% | 100% | 0 | 0 | 0 | 69.62 | 0 | Asep Mulyana: LGS#1 shutdown for check floating switch & TGB oil level sensor.
2023-05-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 93.62 | 0 | No outages (Normal operation).
2023-05-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 117.62 | 0 | No outages (Normal operation).
2023-06-01 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 141.62 | 0 | No outages (Normal operation).
2023-06-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 165.62 | 0 | No outages (Normal operation).
2023-06-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-06-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-06-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-06-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-06-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-06-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-06-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-06-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-06-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-06-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-06-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-06-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-06-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-06-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-06-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-06-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-06-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-06-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-06-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-06-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-06-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-06-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-06-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-06-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-06-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-06-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-06-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-06-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-07-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-07-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-07-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-07-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-07-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-07-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-07-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-07-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-07-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-07-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-07-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-07-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-07-13 | 0.48 | 24 | 0 | 0 | 3.4 | 0 | 3.4 | 20.6 | 85.83% | 100% | 0 | 0 | 0 | 140.6 | 0 | Asep Mulyana: LGS#1 shut down for investigation trip.
2023-07-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 164.6 | 0 | No outages (Normal operation).
2023-07-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-07-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-07-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-07-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-07-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-07-20 | 8 | 24 | 7.35 | 0 | 0 | 0 | 7.35 | 16.65 | 69.38% | 100% | 0 | 0 | 0 | 136.65 | 0 | Asep Mulyana: LGS#1 shut down 8 hrs for PMO HIRA & General PM Check.
2023-07-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 160.65 | 0 | No outages (Normal operation).
2023-07-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-07-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-07-24 | 0.48 | 24 | 0 | 0.07 | 0 | 0 | 0 | 24 | 100% | 99.71% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: - LGS#1 split to aux grid, and back OL supply aux grid. Outage = 0.05 hrs. - LGS#1 split to FCE grid, and back OL supply FCE grid. Outage = 0.02 hrs.
2023-07-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-07-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-07-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-07-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-07-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-07-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-07-31 | 0.48 | 24 | 0 | 0 | 0 | 0.17 | 0.17 | 23.83 | 99.29% | 100% | 0 | 0 | 0 | 71.83 | 0 | Asep Mulyana: Furnace BO occurred, A1G1 CB, Bano 52G1, Bano 52G2, KRB 52G1 CB was trip to Turbine operation by Under Frequency & LGS#1 was trip by over Excitacy.
2023-08-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.83 | 0 | No outages (Normal operation).
2023-08-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 119.83 | 0 | No outages (Normal operation).
2023-08-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.83 | 0 | No outages (Normal operation).
2023-08-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.83 | 0 | No outages (Normal operation).
2023-08-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-08-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-08-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-08-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-08-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-08-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-08-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-08-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-08-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-08-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-08-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-08-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-08-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-08-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-08-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-08-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-08-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-08-22 | 0.48 | 24 | 0 | 0.27 | 0 | 0 | 0 | 24 | 100% | 98.88% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 SNL for split to aux via line#1 // KGS#2
2023-08-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-08-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-08-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-08-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-08-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-08-28 | 0.48 | 24 | 0 | 0.25 | 0 | 0 | 0 | 24 | 100% | 98.96% | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 stand by SNL for split to FCE Grid
2023-08-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-08-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-08-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-09-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-09-02 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 100% | 99.58% | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 put to speed No Load for split to Aux grid
2023-09-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-09-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-09-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-09-06 | 0.48 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 100% | 99.38% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#1 split to FCE grid
2023-09-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-09-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-09-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-09-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-09-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-09-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-09-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-09-14 | 0.48 | 24 | 0 | 0.05 | 0 | 0 | 0 | 24 | 100% | 99.79% | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: LGS#1 split to Bus A12.
2023-09-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-09-16 | 0.48 | 24 | 0 | 0 | 0 | 1.33 | 1.33 | 22.67 | 94.46% | 100% | 0 | 0 | 0 | 22.67 | 0 | Asep Mulyana: Furnace BO occurred, A1G1 CB, A1G3 CB, A3G1 CB, A3G2 CB, Bano 52G1, Bano 52G2, KRB 52G1 CB was trip to Turbine operation.BGS#1-2, KGS#1, LGS#1-3 trip by Over Frequency.
2023-09-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 46.67 | 0 | No outages (Normal operation).
2023-09-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 70.67 | 0 | No outages (Normal operation).
2023-09-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 94.67 | 0 | No outages (Normal operation).
2023-09-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 118.67 | 0 | No outages (Normal operation).
2023-09-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 142.67 | 0 | No outages (Normal operation).
2023-09-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 166.67 | 0 | No outages (Normal operation).
2023-09-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-09-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-09-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-09-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-09-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-09-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-09-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-09-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-10-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-10-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-10-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-10-04 | 0.48 | 24 | 0 | 0 | 0 | 0.28 | 0.28 | 23.72 | 98.83% | 100% | 0 | 0 | 0 | 119.72 | 0 | Asep Mulyana: FCE Grid Blackout
2023-10-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.72 | 0 | No outages (Normal operation).
2023-10-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.72 | 0 | No outages (Normal operation).
2023-10-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-10-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-10-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-10-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-10-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-10-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-10-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-10-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-10-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-10-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-10-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-10-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-10-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-10-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-10-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-10-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-10-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-10-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-10-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-10-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-10-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-10-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-10-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-10-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-10-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-11-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-11-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-11-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-11-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-11-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-11-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-11-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-11-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-11-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-11-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-11-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-11-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-11-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-11-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-11-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-11-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-11-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-11-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-11-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-11-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-11-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-11-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-11-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-11-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-11-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-11-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-11-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-11-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-11-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-11-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-12-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-12-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-12-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-12-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-12-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-12-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-12-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-12-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-12-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-12-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-12-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-12-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-12-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-12-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-12-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-12-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-12-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-12-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-12-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-12-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-12-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-12-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2023-12-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2023-12-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2023-12-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2023-12-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2023-12-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2023-12-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2023-12-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).