## PA_Power
|  | Unit | Week #1 | [6 empty] | Week #2 | [6 empty] | Week #3 | [6 empty] | Week #4 | [6 empty] | Week #5 | [6 empty] | Week #6 | [6 empty] | Week #7 | [6 empty] | Week #8 | [6 empty] | Week #9 | [6 empty] | Week #10 | [6 empty] | Week #11 | [6 empty] | Week #12 | [6 empty] | Week #13 | [6 empty] | Week #14 | [6 empty] | Week #15 | [6 empty] | Week #16 | [6 empty] | Week #17 | [6 empty] | Week #18 | [6 empty] | Week #19 | [6 empty] | Week #20 | [6 empty] | Week #21 | [6 empty] | Week #22 | [6 empty] | Week #23 | [6 empty] | Week #24 | [6 empty] | Week #25 | [6 empty] | Week #26 | [6 empty] | Week #27 | [6 empty] | Week #28 | [6 empty] | Week #29 | [6 empty] | Week #30 | [6 empty] | Week #31 | [6 empty] | Week #32 | [6 empty] | Week #33 | [6 empty] | Week #34 | [6 empty] | Week #35 | [6 empty] | Week #36 | [6 empty] | Week #37 | [6 empty] | Week #38 | [6 empty] | Week #39 | [6 empty] | Week #40 | [6 empty] | Week #41 | [6 empty] | Week #42 | [6 empty] | Week #43 | [6 empty] | Week #44 | [6 empty] | Week #45 | [6 empty] | Week #46 | [6 empty] | Week #47 | [6 empty] | Week #48 | [6 empty] | Week #49 | [6 empty] | Week #50 | [6 empty] | Week #51 | [6 empty] | Week #52 | [6 empty] | Week #53 | [7 empty] | 1
2 | time axis 2019-12-28 to 2021-01-01
3
LGS1 | Forecast Down Time | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 24 | 24 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 14 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8724 | 4
| Total Operating | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8904 | 5 | November
| Actual Plan Outage hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 24 | 0 | 0 | 0 | 11.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 0 | 0 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.34 | 6 | 10.9 | 10.9
| Standby hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.91 | 7
| Force outage by Maintenance | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 8 | 0
| Force outage by Operation | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 5.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.69 | 9 | 0
| Total Down Time Hours | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 24 | 1.7 | 0 | 0 | 11.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 6.92 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 5.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.73 | 0 | 0 | 0 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.67 | 0 | 0 | 0 | 3.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.33 | 10
| Operating Hours | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 7 | 0 | 0 | 22.3 | 24 | 24 | 12.33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 6 | 17.08 | 24 | 24 | 24 | 24 | 23.8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.97 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.1 | 24 | 18.43 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8.27 | 24 | 24 | 24 | 23.63 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14.77 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.15 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 15.33 | 24 | 24 | 24 | 20.08 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14.4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20.9 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 13.1 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8728.67 | 11
| Physical Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 94.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 29.17% | 0% | 0% | 92.92% | 100% | 100% | 51.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 25% | 71.17% | 100% | 100% | 100% | 100% | 99.17% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.88% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.08% | 100% | 76.79% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 34.46% | 100% | 100% | 100% | 98.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 61.54% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 63.88% | 100% | 100% | 100% | 83.67% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 60% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 87.08% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 54.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.21% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.03% | 12
| Utilization of Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.65% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 42.86% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 82.92% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.25% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.38% | 100% | 100% | 100% | 100% | 100% | 100% | 97.08% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.92% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 89.08% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.25% | 100% | 100% | 100% | 100% | 100% | 99.17% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.85% | 13
| Number of external trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 14
| Number of internal trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 15
| Number of Down by Maintenance | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
| MTBF | Day | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 118.7 | 142.7 | 166.7 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 79 | 79 | 79 | 50.65 | 24 | 48 | 60.33 | 84.33 | 108.33 | 132.33 | 156.33 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 150 | 17.08 | 41.08 | 65.08 | 89.08 | 113.08 | 136.88 | 160.88 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 71.985 | 83.985 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 70.1 | 94.1 | 112.53 | 136.53 | 160.53 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 80.27 | 104.27 | 128.27 | 152.27 | 11.815 | 23.815 | 35.815 | 47.815 | 59.815 | 71.815 | 83.815 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 86.77 | 110.77 | 134.77 | 158.77 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 95.15 | 119.15 | 143.15 | 167.15 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 135.33 | 159.33 | 24 | 48 | 68.08 | 92.08 | 92.08 | 92.08 | 96 | 96 | 96 | 96 | 43.2 | 43.2 | 43.2 | 43.2 | 96 | 96 | 96 | 96 | 96 | 92.9 | 92.9 | 92.9 | 92.9 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 85.1 | 85.1 | 85.1 | 85.1 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 95.33 | 95.33 | 95.33 | 95.33 | 96 | 96 | 96 | 96 | 96 |  | 17
| MTTR | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18
|  |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Note on V6: Asep Mulyana: S/D for replace carbon brush & standstill
Note on V7: Asep Mulyana: unit standby
Note on AW6: Asep Mulyana: Major Shut Down Q1-2020 , @07:00-24:00.
Note on AX6: Asep Mulyana: Major Shut Down @00:00-24:00.
Note on AY6: Asep Mulyana: Major Shut Down @00:00-24:00.
Note on AZ9: Asep Mulyana: FCE#1,2,4 were tripped, FCE Grid BO occured. LGS#1-2 tripped to standstill.
Note on BC6: Asep Mulyana: Major Shut Down @00:00-24:00.
Note on BE7: Wahyu Setiadjati: A1-G1CB was opened locally panel, LGS#1 split to thermal auxiliary
Note on CB6: Asep Mulyana: LGS#1 Major Shut Down Q1-2020 for repair oil leaks at Turbine Guide Bearing
Note on CC6: Asep Mulyana: LGS#1 Major Shut Down Q1-2020 for repair oil leaks at Turbine Guide Bearing
Note on CH8: Wahyu Setiadjati: A1G1 & A1G3 CB was open, hydro to FCE grid black out.
Note on DX9: Asep Mulyana: LGS#1 trip by 86N Lock Out (Zoom Air Gap Monitoring Trip) LGS#1 on minimum load for Vibration Trip as required by HIRA.
Note on DZ7: Asep Mulyana: LGS#1 stand by,due to furnace low power.
Note on EW9: Asep Mulyana: FCE Grid Blackout A3L3, A3L4, A3G1, A3G2, A3G3, A3G4, A3L6, BGS 52-G1, BGS 52-G2, KGS 52-G1, A1-G1 & A1-G2 CBs trip. Note: -BGS#1, BGS#2, KGS#1 trip by Bus pro. Energized. -KGS 52-G2 CB still close. -LGS#1 & LGS#3 trip by under Frequency.
Note on EY9: Asep Mulyana: FCE Grid Blackout - BANO 52G1, A3G1, A3G2 CB was open - KRB 52G1 CB was open - LRN A1G1, A1G3 CB was open LGS#1 trip standstill to SNL. by electrical over speed.
Note on FS6: Asep Mulyana: LGS#1 shutdown for Check & Replace Carbon brush.
Note on FW9: Asep Mulyana: Hydro aux grid & FCE grid was black out (BO). Larona A1G1, A1G3 & Bano 52G1, 52G2 CB & Karebbe 52G1, 52G2 & A3G1, A3G2, A3G3, A3G4 A3L3 CB was open
Note on FX7: Asep Mulyana: LGS#1 standby: put to speed no load for prapare spilt to FCE’ Grid.
Note on HI6: Asep Mulyana: LGS#1 SHUTDOWN : - Turn off for 160% mech. EOS take data di dention & general pm check. - LGS#1 delay time do to adjusting vibration sistem
Note on JF9: Asep Mulyana: LRN A1-G1 CB & LRN A1-G3 CB were opened and tripped by oper speed 115% energized. Hydro to FCE’s grid BO Note: FCE#3 trip
Note on JG7: Asep Mulyana: LGS#1 back inservice supply to FCE’s grid.
Note on JN7: Asep Mulyana: LGS#1 Unit Standby, prepare split to AUX grid
Note on JV6: Asep Mulyana: LGS#1 shutted down for HIRA & PM Check.
Note on JZ6: Asep Mulyana: LGS#1 turn off for 125% mech. EOS take data di dention & general pm check.
Note on KA7: Asep Mulyana: - LGS#1 put to Speed No Load prepared bus transfer for supply FCE grid via Bus A11//A22 - LGS#1 standby to SNL for prepare split to FCE’s grid
Note on KH9: Asep Mulyana: Hydro total BO. A1G1, A1G2, A1G3, BLN 52G2, KRB 52G1, 52G2 & A3L3 CB was open. LGS#1 trip by O/Speed caused penstock intake trip to fully close. Mech O/S device on turbine pit was operated. LGS#2 trip by O/speed. Alarm on DRS panel over frequency. LGS#3 trip by O/Speed. Relay 86E energize
Note on KQ8: Asep Mulyana: LGS#1 shutdown unplan for black out investigation.
Note on KV7: Asep Mulyana: LGS#1 put to SNL for supply Aux grid and back inservice supply to Auxs Grid
Note on LL6: Asep Mulyana: LGS#1 shut down for PM Check Adjust Mech. OS to 135% (HIRA)
Note on LP7: Asep Mulyana: 1. LGS#1 put to supply FCE Grid and then back on line to FCE grid (0.08 hrs) 2. LGS#1 SNL for split to aux grid then back on line to supply aux grid (0.12 hrs)
Note on NB9: Asep Mulyana: Hydro Total Blackout

## PA_Power_Summary
Date | Planned Down Time (Hour) | Total Operating (Hour) | Actual Plan Outage hrs (Hour) | Standby hrs (Hour) | Force outage by Maintenance (Hour) | Force outage by Operation (Hour) | Total Down Time Hours (Hour) | Operating Hours (Hour) | Physical Availability (%) | Utilization of Availability (%) | Number of external trip/failure (Times) | Number of internal trip/failure (Times) | Number of Down by Maintenance (Times) | MTBF (Day) | MTTR (Hour) | Remarks | Category | LGS Status | Activity or Problem | Related Component | Note
2019-12-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2019-12-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2019-12-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2019-12-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-01-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-01-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-01-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-01-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-01-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-01-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-01-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-01-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-01-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-01-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-01-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-01-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-01-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-01-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-01-15 | 20 | 24 | 1.3 | 0.08 | 0 | 0 | 1.3 | 22.7 | 94.58% | 99.65% | 0 | 0 | 0 | 118.7 | 0 | Asep Mulyana: S/D for replace carbon brush & standstill Asep Mulyana: unit standby | Actual Plant Outage | Shutdown | Repair Component | Carbon Brush
2020-01-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 142.7 | 0 | No outages (Normal operation).
2020-01-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 166.7 | 0 | No outages (Normal operation).
2020-01-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-01-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-01-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-01-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-01-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-01-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-01-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-01-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-01-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-01-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-01-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-01-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-01-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-01-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-02-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-02-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-02-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-02-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-02-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-02-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-02-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-02-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-02-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-02-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-02-11 | 0 | 24 | 17 | 4 | 0 | 0 | 17 | 7 | 29.17% | 42.86% | 0 | 0 | 0 | 79 | 0 | Asep Mulyana: Major Shut Down Q1-2020 , @07:00-24:00. | Actual Plant Outage | Shutdown | Major Shutdown | LGS
2020-02-12 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 79 | 0 | Asep Mulyana: Major Shut Down @00:00-24:00. | Actual Plant Outage | Shutdown | Major Shutdown | LGS
2020-02-13 | 0 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0% | 0% | 0 | 0 | 0 | 79 | 0 | Asep Mulyana: Major Shut Down @00:00-24:00. | Actual Plant Outage | Shutdown | Major Shutdown | LGS
2020-02-14 | 24 | 24 | 0 | 0 | 0 | 1.7 | 1.7 | 22.3 | 92.92% | 100% | 0 | 1 | 0 | 50.65 | 0 | Asep Mulyana: FCE#1,2,4 were tripped, FCE Grid BO occured. LGS#1-2 tripped to standstill. | Operation | Tripped to Standstill | Grid Blackout | FCE Grid
2020-02-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-02-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-02-17 | 0 | 24 | 11.67 | 0 | 0 | 0 | 11.67 | 12.33 | 51.38% | 100% | 0 | 0 | 0 | 60.33 | 0 | Asep Mulyana: Major Shut Down @00:00-24:00. | Actual Plant Outage | Shutdown | Major Shutdown | LGS
2020-02-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 84.33 | 0 | No outages (Normal operation).
2020-02-19 | 24 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 100% | 99.58% | 0 | 0 | 0 | 108.33 | 0 | Wahyu Setiadjati: A1-G1CB was opened locally panel, LGS#1 split to thermal auxiliary | Standby | Put on Standby | Prepare Split to Grid | A1-G1CB
2020-02-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 132.33 | 0 | No outages (Normal operation).
2020-02-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 156.33 | 0 | No outages (Normal operation).
2020-02-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-02-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-02-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-02-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-02-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-02-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-02-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-02-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-03-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-03-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-03-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-03-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-03-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-03-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-03-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-03-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-03-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-03-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-03-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-03-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-03-13 | 0 | 24 | 18 | 0 | 0 | 0 | 18 | 6 | 25% | 100% | 0 | 0 | 0 | 150 | 0 | Asep Mulyana: LGS#1 Major Shut Down Q1-2020 for repair oil leaks at Turbine Guide Bearing | Actual Plant Outage | Shutdown | Repair Component | Turbine Guide Bearing
2020-03-14 | 14 | 24 | 6.92 | 0 | 0 | 0 | 6.92 | 17.08 | 71.17% | 100% | 0 | 0 | 0 | 17.08 | 0 | Asep Mulyana: LGS#1 Major Shut Down Q1-2020 for repair oil leaks at Turbine Guide Bearing | Actual Plant Outage | Shutdown | Repair Component | Turbine Guide Bearing
2020-03-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 41.08 | 0 | No outages (Normal operation).
2020-03-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 65.08 | 0 | No outages (Normal operation).
2020-03-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 89.08 | 0 | No outages (Normal operation).
2020-03-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 113.08 | 0 | No outages (Normal operation).
2020-03-19 | 24 | 24 | 0 | 0 | 0.2 | 0 | 0.2 | 23.8 | 99.17% | 100% | 0 | 0 | 0 | 136.88 | 0 | Wahyu Setiadjati: A1G1 & A1G3 CB was open, hydro to FCE grid black out. | Maintenance | Put on Standby | Grid Blackout | FCE Grid
2020-03-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 160.88 | 0 | No outages (Normal operation).
2020-03-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-03-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-03-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-03-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-03-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-03-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-03-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-03-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-03-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-03-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-03-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-04-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-04-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-04-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-04-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-04-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-04-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-04-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-04-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-04-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-04-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-04-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-04-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-04-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-04-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-04-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-04-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-04-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-04-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-04-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-04-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-04-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-04-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-04-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-04-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-04-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-04-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-04-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-04-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-04-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-04-30 | 24 | 24 | 0 | 0 | 0 | 0.03 | 0.03 | 23.97 | 99.88% | 100% | 0 | 1 | 0 | 71.985 | 0 | Asep Mulyana: LGS#1 trip by 86N Lock Out (Zoom Air Gap Monitoring Trip) LGS#1 on minimum load for Vibration Trip as required by HIRA. | Maintenance | Trip | Equipment Trip | Guide Bearing | Zoom Air Gap Monitoring Trip
2020-05-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 83.985 | 0 | No outages (Normal operation).
2020-05-02 | 24 | 24 | 0 | 4.1 | 0 | 0 | 0 | 24 | 100% | 82.92% | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 stand by,due to furnace low power. | Standby | Put on Standby | Furnace Low Power | Furnace
2020-05-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-05-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-05-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-05-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-05-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-05-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-05-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-05-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-05-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-05-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-05-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-05-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-05-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-05-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-05-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-05-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-05-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-05-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-05-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-05-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-05-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-05-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-05-25 | 24 | 24 | 0 | 0 | 0 | 1.9 | 1.9 | 22.1 | 92.08% | 100% | 2 | 0 | 0 | 70.1 | 0 | Asep Mulyana: FCE Grid Blackout A3L3, A3L4, A3G1, A3G2, A3G3, A3G4, A3L6, BGS 52-G1, BGS 52-G2, KGS 52-G1, A1-G1 & A1-G2 CBs trip. Note: -BGS#1, BGS#2, KGS#1 trip by Bus pro. Energized. -KGS 52-G2 CB still close. -LGS#1 & LGS#3 trip by under Frequency. | Operation | Trip | Grid Blackout | FCE Grid
2020-05-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 94.1 | 0 | No outages (Normal operation).
2020-05-27 | 24 | 24 | 0 | 0 | 0 | 5.57 | 5.57 | 18.43 | 76.79% | 100% | 1 | 0 | 0 | 112.53 | 0 | Asep Mulyana: FCE Grid Blackout - BANO 52G1, A3G1, A3G2 CB was open - KRB 52G1 CB was open - LRN A1G1, A1G3 CB was open LGS#1 trip standstill to SNL. by electrical over speed. | Operation | Speed No Load | Grid Blackout | FCE Grid
2020-05-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 136.53 | 0 | No outages (Normal operation).
2020-05-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 160.53 | 0 | No outages (Normal operation).
2020-05-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-05-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-06-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-06-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-06-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-06-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-06-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-06-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-06-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-06-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-06-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-06-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-06-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-06-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-06-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-06-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-06-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-06-16 | 8 | 24 | 15.73 | 0 | 0 | 0 | 15.73 | 8.27 | 34.46% | 100% | 0 | 0 | 0 | 80.27 | 0 | Asep Mulyana: LGS#1 shutdown for Check & Replace Carbon brush. | Actual Plant Outage | Shutdown | Check and Repair | Carbon Brush
2020-06-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 104.27 | 0 | No outages (Normal operation).
2020-06-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 128.27 | 0 | No outages (Normal operation).
2020-06-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 152.27 | 0 | No outages (Normal operation).
2020-06-20 | 24 | 24 | 0 | 0 | 0 | 0.37 | 0.37 | 23.63 | 98.46% | 100% | 0 | 1 | 0 | 11.815 | 0 | Asep Mulyana: Hydro aux grid & FCE grid was black out (BO). Larona A1G1, A1G3 & Bano 52G1, 52G2 CB & Karebbe 52G1, 52G2 & A3G1, A3G2, A3G3, A3G4 A3L3 CB was open | Operation | Unconfirmed | Grid Blackout | FCE Grid; Auxiliary Grid
2020-06-21 | 24 | 24 | 0 | 0.18 | 0 | 0 | 0 | 24 | 100% | 99.25% | 0 | 0 | 0 | 23.815 | 0 | Asep Mulyana: LGS#1 standby: put to speed no load for prapare spilt to FCE’ Grid. | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2020-06-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 35.815 | 0 | No outages (Normal operation).
2020-06-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 47.815 | 0 | No outages (Normal operation).
2020-06-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 59.815 | 0 | No outages (Normal operation).
2020-06-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 71.815 | 0 | No outages (Normal operation).
2020-06-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 83.815 | 0 | No outages (Normal operation).
2020-06-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-06-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-06-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-06-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-07-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-07-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-07-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-07-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-07-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-07-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-07-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-07-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-07-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-07-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-07-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-07-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-07-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-07-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-07-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-07-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-07-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-07-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-07-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-07-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-07-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-07-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-07-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-07-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-07-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-07-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-07-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-07-28 | 14 | 24 | 9.23 | 0 | 0 | 0 | 9.23 | 14.77 | 61.54% | 100% | 0 | 0 | 0 | 86.77 | 0 | Asep Mulyana: LGS#1 SHUTDOWN : - Turn off for 160% mech. EOS take data di dention & general pm check. - LGS#1 delay time do to adjusting vibration sistem | Actual Plant Outage | Shutdown | PM Check | Vibration system
2020-07-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 110.77 | 0 | No outages (Normal operation).
2020-07-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 134.77 | 0 | No outages (Normal operation).
2020-07-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 158.77 | 0 | No outages (Normal operation).
2020-08-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-08-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-08-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-08-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-08-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-08-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-08-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-08-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-08-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-08-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-08-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-08-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-08-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-08-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-08-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-08-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-08-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-08-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-08-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-08-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-08-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-08-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-08-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-08-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-08-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-08-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-08-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-08-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-08-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-08-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-08-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-09-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-09-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-09-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-09-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-09-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-09-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-09-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-09-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-09-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-09-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-09-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-09-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-09-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-09-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-09-15 | 24 | 24 | 0 | 0 | 0 | 0.85 | 0.85 | 23.15 | 96.46% | 100% | 2 | 0 | 0 | 95.15 | 0 | Asep Mulyana: LRN A1-G1 CB & LRN A1-G3 CB were opened and tripped by oper speed 115% energized. Hydro to FCE’s grid BO Note: FCE#3 trip | Actual Plant Outage | Unconfirmed | Grid Blackout | FCE Grid
2020-09-16 | 24 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 100% | 99.38% | 0 | 0 | 0 | 119.15 | 0 | Asep Mulyana: LGS#1 back inservice supply to FCE’s grid. | Actual Plant Outage | Put on Standby | Back in Supply to Grid | FCE Grid
2020-09-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 143.15 | 0 | No outages (Normal operation).
2020-09-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 167.15 | 0 | No outages (Normal operation).
2020-09-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-09-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-09-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-09-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-09-23 | 24 | 24 | 0 | 0.7 | 0 | 0 | 0 | 24 | 100% | 97.08% | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#1 Unit Standby, prepare split to AUX grid | Standby | Put on Standby | Prepare Split to Grid | Auxiliary Grid
2020-09-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2020-09-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2020-09-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-09-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-09-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2020-09-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-09-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2020-10-01 | 16 | 24 | 8.67 | 0 | 0 | 0 | 8.67 | 15.33 | 63.88% | 100% | 0 | 0 | 0 | 135.33 | 0 | Asep Mulyana: LGS#1 shutted down for HIRA & PM Check. | Actual Plant Outage | Shutdown | PM Check; HIRA | LGS
2020-10-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 159.33 | 0 | No outages (Normal operation).
2020-10-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2020-10-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2020-10-05 | 20 | 24 | 3.92 | 0 | 0 | 0 | 3.92 | 20.08 | 83.67% | 100% | 0 | 0 | 0 | 68.08 | 0 | Asep Mulyana: LGS#1 turn off for 125% mech. EOS take data di dention & general pm check. | Actual Plant Outage | Shutdown | PM Check | Vibration system
2020-10-06 | 24 | 24 | 0 | 0.5 | 0 | 0 | 0 | 24 | 100% | 97.92% | 0 | 0 | 0 | 92.08 | 0 | Asep Mulyana: - LGS#1 put to Speed No Load prepared bus transfer for supply FCE grid via Bus A11//A22 - LGS#1 standby to SNL for prepare split to FCE’s grid | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2020-10-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 92.08 | 0 | No outages (Normal operation).
2020-10-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 92.08 | 0 | No outages (Normal operation).
2020-10-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-13 | 24 | 24 | 0 | 0 | 0 | 9.6 | 9.6 | 14.4 | 60% | 100% | 0 | 1 | 0 | 43.2 | 0 | Asep Mulyana: Hydro total BO. A1G1, A1G2, A1G3, BLN 52G2, KRB 52G1, 52G2 & A3L3 CB was open. LGS#1 trip by O/Speed caused penstock intake trip to fully close. Mech O/S device on turbine pit was operated. LGS#2 trip by O/speed. Alarm on DRS panel over frequency. LGS#3 trip by O/Speed. Relay 86E energize | Operation | Total Blackout | Equipment Trip | Penstock
2020-10-14 | 24 | 24 | 0 | 2.62 | 0 | 0 | 0 | 24 | 100% | 89.08% | 0 | 0 | 0 | 43.2 | 0 | No outages (Normal operation).
2020-10-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 43.2 | 0 | No outages (Normal operation).
2020-10-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 43.2 | 0 | No outages (Normal operation).
2020-10-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-22 | 24 | 24 | 0 | 0 | 3.1 | 0 | 3.1 | 20.9 | 87.08% | 100% | 0 | 0 | 0 | 92.9 | 0 | Asep Mulyana: LGS#1 shutdown unplan for black out investigation. | Maintenance | Shutdown (Unplanned) | Check and Repair | LGS | Black Out Investigation
2020-10-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 92.9 | 0 | No outages (Normal operation).
2020-10-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 92.9 | 0 | No outages (Normal operation).
2020-10-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 92.9 | 0 | No outages (Normal operation).
2020-10-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-27 | 24 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 100% | 99.58% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 put to SNL for supply Aux grid and back inservice supply to Auxs Grid | Standby | Speed No Load | Back in Supply to Grid | Auxiliary Grid
2020-10-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-10-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-10 | 24 | 24 | 0 | 0.18 | 0 | 0 | 0 | 24 | 100% | 99.25% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-12 | 16 | 24 | 10.9 | 0 | 0 | 0 | 10.9 | 13.1 | 54.58% | 100% | 0 | 0 | 0 | 85.1 | 0 | Asep Mulyana: LGS#1 shut down for PM Check Adjust Mech. OS to 135% (HIRA) | Actual Plant Outage | Shutdown | PM Check | Vibration system
2020-11-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 85.1 | 0 | No outages (Normal operation).
2020-11-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 85.1 | 0 | No outages (Normal operation).
2020-11-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 85.1 | 0 | No outages (Normal operation).
2020-11-16 | 24 | 24 | 0 | 0.2 | 0 | 0 | 0 | 24 | 100% | 99.17% | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: 1. LGS#1 put to supply FCE Grid and then back on line to FCE grid (0.08 hrs) 2. LGS#1 SNL for split to aux grid then back on line to supply aux grid (0.12 hrs) | Standby | Put on Standby | Back in Supply to Grid | Auxiliary Grid
2020-11-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-24 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-11-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-01 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-02 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-03 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-04 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-05 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-06 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-07 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-08 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-09 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-10 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-11 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-22 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-23 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-24 | 24 | 24 | 0 | 0 | 0 | 0.67 | 0.67 | 23.33 | 97.21% | 100% | 1 | 0 | 0 | 95.33 | 0 | Asep Mulyana: Hydro Total Blackout | Operation | Total Blackout
2020-12-25 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.33 | 0 | No outages (Normal operation).
2020-12-26 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.33 | 0 | No outages (Normal operation).
2020-12-27 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 95.33 | 0 | No outages (Normal operation).
2020-12-28 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-29 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-30 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2020-12-31 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 100% | 100% | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).