## PA_Power
|  | Unit | Week #1 | [6 empty] | Week #2 | [6 empty] | Week #3 | [6 empty] | Week #4 | [6 empty] | Week #5 | [6 empty] | Week #6 | [6 empty] | Week #7 | [6 empty] | Week #8 | [6 empty] | Week #9 | [6 empty] | Week #10 | [6 empty] | Week #11 | [6 empty] | Week #12 | [6 empty] | Week #13 | [6 empty] | Week #14 | [6 empty] | Week #15 | [6 empty] | Week #16 | [6 empty] | Week #17 | [6 empty] | Week #18 | [6 empty] | Week #19 | [6 empty] | Week #20 | [6 empty] | Week #21 | [6 empty] | Week #22 | [6 empty] | Week #23 | [6 empty] | Week #24 | [6 empty] | Week #25 | [6 empty] | Week #26 | [6 empty] | Week #27 | [6 empty] | Week #28 | [6 empty] | Week #29 | [6 empty] | Week #30 | [6 empty] | Week #31 | [6 empty] | Week #32 | [6 empty] | Week #33 | [6 empty] | Week #34 | [6 empty] | Week #35 | [6 empty] | Week #36 | [6 empty] | Week #37 | [6 empty] | Week #38 | [6 empty] | Week #39 | [6 empty] | Week #40 | [6 empty] | Week #41 | [6 empty] | Week #42 | [6 empty] | Week #43 | [6 empty] | Week #44 | [6 empty] | Week #45 | [6 empty] | Week #46 | [6 empty] | Week #47 | [6 empty] | Week #48 | [6 empty] | Week #49 | [6 empty] | Week #50 | [6 empty] | Week #51 | [6 empty] | Week #52 | [6 empty] | 1
2 | time axis 2022-01-01 to 2022-12-30
3
LGS1 | Planned Down Time | Hour | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 4 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 2 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 8 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 2 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 24 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 24 | 24 | 10 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 4 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 10 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 12 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 24 | 24 | 24 | 24 | 0.48 | 8 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 4 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 8 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 4
| Total Operating | Hour | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 5
| Actual Plan Outage hrs | Hour | 0 | 0 | 0 | 0 | 0 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9166 | 24 | 24 | 24 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5 | 24 | 24 | 24 | 19.03 | 0 | 0 | 0 | 0 | 0 | 21.15 | 24 | 14.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6
| Standby hrs | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0.17 | 0 | 0 | 0 | 0.28 | 0 | 0 | 0 | 0 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.08 | 0 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 1.8 | 0 | 0 | 0.17 | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0.48 | 0 | 0 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
| Force outage by Maintenance | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 20.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 3.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
| Force outage by Operation | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.43 | 0 | 0 | 0 | 0 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9
| Total Down Time Hours | Hour | 0 | 0 | 0 | 0 | 0 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 24 | 0 | 20.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9166 | 24 | 24 | 24 | 13.93 | 0 | 0 | 0 | 0 | 0.48 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5 | 24 | 24 | 24 | 19.03 | 0 | 0 | 0 | 0 | 0 | 21.15 | 24 | 14.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.83 | 9.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 3.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
| Operating Hours | Hour | 24 | 24 | 24 | 24 | 24 | 20.99 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 17.28 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20.2 | 24 | 24 | 24 | 24 | 0 | 24 | 3.15 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 6.0834 | 0 | 0 | 0 | 10.07 | 24 | 24 | 24 | 24 | 23.52 | 24 | 24 | 24 | 24 | 23.68 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 5.5 | 0 | 0 | 0 | 4.97 | 24 | 24 | 24 | 24 | 24 | 2.85 | 0 | 9.28 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 12.1 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.98 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 7.17 | 14.03 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23.68 | 24 | 24 | 24 | 24 | 24 | 20.97 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22.22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16.75 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 11
| Physical Availability | % | 100% | 100% | 100% | 100% | 100% | 87.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 72% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 84.17% | 100% | 100% | 100% | 100% | 0% | 100% | 13.12% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 25.35% | 0% | 0% | 0% | 41.96% | 100% | 100% | 100% | 100% | 98% | 100% | 100% | 100% | 100% | 98.67% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 22.92% | 0% | 0% | 0% | 20.71% | 100% | 100% | 100% | 100% | 100% | 11.88% | 0% | 38.67% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 50.42% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 95.75% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 29.88% | 58.46% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.67% | 100% | 100% | 100% | 100% | 100% | 87.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 92.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 69.79% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 12
| Utilization of Availability | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 100% | 99.29% | 100% | 100% | 100% | 98.83% | 100% | 100% | 100% | 100% | 97.62% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.25% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.46% | 100% | 100% | 100% | 100% | 100% | 99.38% | 100% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0% | 100% | 96.75% | 100% | 100% | 99.08% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.79% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 96.79% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 97.21% | 100% | 100% | 100% | 99.07% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.67% | 100% | 100% | 100% | 99.5% | 100% | 100% | 100% | 100% | 100% | 99.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 92.5% | 100% | 100% | 99.29% | 99.46% | 100% | 100% | 100% | 100% | 100% | 100% | 99.17% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.29% | 100% | 100% | 100% | 100% | 100% | 99.58% | 100% | 100% | 98% | 100% | 100% | 99.28% | 100% | 100% | 100% | 100% | 100% | 100% | 99.71% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 13
| Number of external trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14
| Number of internal trip/failure | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15
| Number of Down by Maintenance | Times | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16
| MTBF | Day | 24 | 48 | 72 | 96 | 120 | 140.99 | 164.99 | 24 | 48 | 72 | 96 | 120 | 144 | 167.22 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 137.28 | 161.28 | 24 | 48 | 72 | 96 | 120 | 144 | 164.2 | 24 | 48 | 72 | 96 | 96 | 120 | 123.15 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 78.0834 | 78.0834 | 78.0834 | 78.0834 | 3.3567 | 11.3567 | 19.3567 | 27.3567 | 35.3567 | 43.1967 | 51.1967 | 24 | 48 | 72 | 95.68 | 119.68 | 143.68 | 167.68 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 53.5 | 53.5 | 53.5 | 53.5 | 58.47 | 24 | 48 | 72 | 96 | 120 | 122.85 | 122.85 | 9.28 | 33.28 | 57.28 | 81.28 | 105.28 | 129.28 | 153.28 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 84.1 | 108.1 | 132.1 | 156.1 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 22.98 | 46.98 | 70.98 | 94.98 | 118.98 | 142.98 | 166.98 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 127.17 | 141.2 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 167.68 | 24 | 48 | 72 | 96 | 120 | 140.97 | 164.97 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 118.22 | 142.22 | 166.22 | 24 | 48 | 72 | 96 | 120 | 136.75 | 160.75 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 24 | 48 | 72 | 96 | 120 | 144 | 168 | 17
| MTTR | Hour | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18
|  |  | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Note on I6: Asep Mulyana: LGS#1 shutted down for check GOP#1-2 control.
Note on Q6: Asep Mulyana: LGS#1 was shuted off for check alarm on Multilin
Note on AD6: Rajab: LGS#1 Sdown for general pm check & replace SPMD & MTX protection relay T60 integration communication.
Note on AL6: Asep Mulyana: LGS#1 shut down for check & repair alarm on DRS panel & inspection generator by instrument & electik crew.
Note on AL8: Asep Mulyana: LGS#1 shut down for check & repair alarm on DRS panel & inspection generator by instrument & electik crew.
Note on AQ6: Asep Mulyana: LGS#1 Shutdown stoplog install
Note on AS8: Asep Mulyana: LGS#1 was stop due to replace Carbon brush.
Note on AT7: Asep Mulyana: LGS#1 standby to SNL for prepare split to Aux. grid
Note on AX7: Asep Mulyana: LGS#1 SNL for split to FCE grid due to line#2 will be isolated.
Note on BC7: Asep Mulyana: LGS#1 put on SNL due to prepare splite to Auxiliary grid
Note on CA7: Asep Mulyana: LGS#1 put to speed no load for transfer to FCE’s grid
Note on CF6: Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement.
Note on CG6: Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement.
Note on CI6: Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement.
Note on CJ6: Asep Mulyana: - LGS#1 shut down for MTX#1 Oil Conservator Bag replacement. - LGS#1 back in service for supply FCE’s grid. Outage : 2.50 hrs
Note on CJ9: Asep Mulyana: LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip. - LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip.
Note on CO9: Asep Mulyana: Furnace grid Blackout A1-G1CB, A1-G3CB, BLBN 52-G1CB-52-G2CB & KGS 52-G1CB were tripped by over frequency relay energized.
Note on CT8: Asep Mulyana: LGS#1 shutdown for servomotor leaks
Note on DQ7: Wahyu Setiadjati: LGS#1 put on SNL for split to Aux grid
Note on EI7: Asep Mulyana: LGS#1 put to standby for split to Thermal auxiliaries.
Note on EO7: Asep Mulyana: LGS#1 put standby for split to FCE’s grid
Note on EP6: Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM.
Note on EQ6: Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM.
Note on ER6: Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM.
Note on ES6: Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM.
Note on ET6: Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM.
Note on EZ4: Wahyu Setiadjati: Total shutdown, inspection of canal lining
Note on EZ6: Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check.
Note on FA6: Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check.
Note on FB6: Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check.
Note on FC7: Asep Mulyana: LGS#1 put standby for thermal split bus
Note on FF7: Asep Mulyana: LGS#1 back online & supply aux grid (23:59 A1G1CB open). Outage : 0.22 hrs
Note on HI8: Asep Mulyana: LGS#1 shutdown for Card module 64R replacement & general PM Check.
Note on HP7: Asep Mulyana: LGS#1 standby for spilt to aux grid.
Note on IH9: Asep Mulyana: Total Blackout Occured. BGS 52-G2, KGS 52-G1, KGS 52-G2, A1-G1, A1-G2, A1-G3, A3G1,A3G2 CB trip. Note: Thermal A2L2 suddenly Trip.
Note on IJ7: Wahyu Setiadjati: Swithcing
Note on IX7: Asep Mulyana: - LGS#1 split to FCE grid outage 0.30 hrs - LGS#1 SNL for split to Aux grid. Outage 0.37 hrs
Note on JA6: Asep Mulyana: LGS#1 shutdown for servomotor adjust, Carbon brush replacement & General PM Check.
Note on JB7: Asep Mulyana: LGS#1 back on line via line#1 to supply aux grid // KGS#2. Outage: 0.13 hrs
Note on JB8: Asep Mulyana: LGS#1 back on line to supply FCE grid (load performa test to 60 MW before split to Aux grid). Outage: 9.97 hrs
Note on JS7: Asep Mulyana: LGS#1 prepare split to FCE grid
Note on JW7: Asep Mulyana: LGS#1 prepare split to Aux grid
Note on KC7: Asep Mulyana: LGS#1 SNL for split to FCE grid
Note on KD8: Asep Mulyana: LGS#1 was stop via 4/CS / Emergency stop on HMI on load 30 MW due to penstock vibration check on load rejection test
Note on KJ8: Asep Mulyana: - LGS#1 shut down for check A1G1 CB kirk key. Outage 3.02 hrs - LGS#1 was tripped via Emergency Stop HMI Larona. Outage 0.01 hrs
Note on KR7: Asep Mulyana: LGS#1 SNL for split to aux grid.
Note on KZ7: Asep Mulyana: LGS#1 standby for prepare split to FCE grid
Note on LB7: Asep Mulyana: - LGS#1 put on standby due to prepare split to FCE’s grid. - LGS#1 put on standby due to prepare split to Aux grid.
Note on LE7: Asep Mulyana: - LGS#1 put standby for adding a delay timer (3 second) on the penstock gate limit switch.
Note on LF7: Asep Mulyana: - LGS#1 standby for prepare split to FCE grid due to LGS#2 emergency shut down. - LGS#1 standby for prepare split to Auxiliary gri
Note on LG4: Wahyu Setiadjati: Carbon Brush Dust Extractor
Note on LM7: Asep Mulyana: LGS#1 SNL for split to FCE grid
Note on MB7: Asep Mulyana: LGS#1 put to SNL for prepared split to Auxiliary Grid
Note on MF8: Asep Mulyana: LGS#1 shutdown for carbon brush replacement.
Note on MH7: Asep Mulyana: LGS#1 standby for split to FCE grid - LGS#1 standby for split to Aux grid
Note on MK7: Asep Mulyana: LGS#1 put on standby prepare split to FCE’s grid
Note on MN6: Asep Mulyana: LGS#1 shut down for PM Check Hira Turbine & Penstock
Note on MN7: Asep Mulyana: - LGS#2 prepare split to FCE grid - LGS#2 prepare split to aux grid
Note on MU7: Asep Mulyana: LGS#1 prepare split to Aux grid

## PA_Power_Summary
Date | Planned Down Time (Hour) | Total Operating (Hour) | Actual Plan Outage hrs (Hour) | Standby hrs (Hour) | Force outage by Maintenance (Hour) | Force outage by Operation (Hour) | Total Down Time Hours (Hour) | Operating Hours (Hour) | Physical Availability (%) | Utilization of Availability (%) | Number of external trip/failure (Times) | Number of internal trip/failure (Times) | Number of Down by Maintenance (Times) | MTBF (Day) | MTTR (Hour) | Remarks | Category | LGS Status | Activity or Problem | Related Component | Note
2022-01-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-01-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-01-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-01-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-01-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-01-06 | 4 | 24 | 3.01 | 0 | 0 | 0 | 3.01 | 20.99 | 0.87458 | 1 | 0 | 0 | 0 | 140.99 | 0 | Asep Mulyana: LGS#1 shutted down for check GOP#1-2 control. | Actual Plant Outage | Shutdown | Check and Repair | GOP
2022-01-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 164.99 | 0 | No outages (Normal operation).
2022-01-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-01-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-01-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-01-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-01-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-01-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-01-14 | 2 | 24 | 0.78 | 0 | 0 | 0 | 0.78 | 23.22 | 0.9675 | 1 | 0 | 0 | 0 | 167.22 | 0 | Asep Mulyana: LGS#1 was shuted off for check alarm on Multilin | Actual Plant Outage | Shutted Off | Check and Repair | Alarm
2022-01-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-01-16 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-01-17 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-01-18 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-01-19 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-01-20 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-01-21 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-01-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-01-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-01-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-01-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-01-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-01-27 | 8 | 24 | 6.72 | 0 | 0 | 0 | 6.72 | 17.28 | 0.72 | 1 | 0 | 0 | 0 | 137.28 | 0 | Rajab: LGS#1 Sdown for general pm check & replace SPMD & MTX protection relay T60 integration communication. | Actual Plant Outage | Shutdown | Check and Repair | MTX Protection
2022-01-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 161.28 | 0 | No outages (Normal operation).
2022-01-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-01-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-01-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-02-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-02-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-02-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-02-04 | 2 | 24 | 1.9 | 0 | 1.9 | 0 | 3.8 | 20.2 | 0.84167 | 1 | 0 | 0 | 0 | 164.2 | 0 | Asep Mulyana: LGS#1 shut down for check & repair alarm on DRS panel & inspection generator by instrument & electik crew. Asep Mulyana: LGS#1 shut down for check & repair alarm on DRS panel & inspection generator by instrument & electik crew. | Actual Plant Outage | Shutdown | Check and Repair | Alarm
2022-02-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-02-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-02-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-02-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-02-09 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 Shutdown stoplog install | Actual Plant Outage | Shutdown | Check and Repair | Stoplog Installation
2022-02-10 | 24 | 24 | 0 | 24 | 0 | 0 | 0 | 24 | 1 | 0 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-02-11 | 24 | 24 | 0 | 0 | 20.85 | 0 | 20.85 | 3.15 | 0.13125 | 1 | 0 | 0 | 0 | 123.15 | 0 | Asep Mulyana: LGS#1 was stop due to replace Carbon brush. | Maintenance | Stop | Repair Component | Carbon Brush
2022-02-12 | 0.48 | 24 | 0 | 0.17 | 0 | 0 | 0 | 24 | 1 | 0.99292 | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 standby to SNL for prepare split to Aux. grid
2022-02-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-02-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-02-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-02-16 | 0.48 | 24 | 0 | 0.28 | 0 | 0 | 0 | 24 | 1 | 0.98833 | 0 | 0 | 0 | 120 | 0 | Asep Mulyana: LGS#1 SNL for split to FCE grid due to line#2 will be isolated. | Standby | Speed No Load | Prepare Split to Grid | FCE Grid | Line#2 will be isolated
2022-02-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-02-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-02-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-02-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-02-21 | 0.48 | 24 | 0 | 0.57 | 0 | 0 | 0 | 24 | 1 | 0.97625 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 put on SNL due to prepare splite to Auxiliary grid | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2022-02-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-02-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-02-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-02-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-02-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-02-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-02-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-03-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-03-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-03-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-03-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-03-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-03-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-03-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-03-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-03-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-03-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-03-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-03-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-03-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-03-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-03-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-03-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-03-17 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 1 | 0.99583 | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: LGS#1 put to speed no load for transfer to FCE’s grid | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2022-03-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-03-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-03-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-03-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-03-22 | 24 | 24 | 17.9166 | 0 | 0 | 0 | 17.9166 | 6.0834 | 0.25348 | 1 | 0 | 0 | 0 | 78.0834 | 0 | Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement. | Actual Plant Outage | Shutdown | Repair Component | MTX #1 Oil Conservator
2022-03-23 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0834 | 0 | Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement. | Actual Plant Outage | Shutdown | Repair Component | MTX #1 Oil Conservator
2022-03-24 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0834 | 0 | No information (Actual Plant Outage) | Actual Plant Outage | Unconfirmed
2022-03-25 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 78.0834 | 0 | Asep Mulyana: LGS#1 shut down for MTX#1 Oil Conservator Bag replacement. | Actual Plant Outage | Shutdown | Repair Component | MTX #1 Oil Conservator
2022-03-26 | 10 | 24 | 2.5 | 0 | 0 | 11.43 | 13.93 | 10.07 | 0.41958 | 1 | 0 | 2 | 0 | 3.3567 | 0 | Asep Mulyana: - LGS#1 shut down for MTX#1 Oil Conservator Bag replacement. - LGS#1 back in service for supply FCE’s grid. Outage : 2.50 hrs Asep Mulyana: LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip. - LGS#1 suddenly trip by 86N due to Rotor shaft Current stage 2 high trip. | Operation | Shutdown, Back in Service, Trip | Repair Component, Back in Service to Grid, Equipment Trip | MTX #1 Oil Conservator, FCE Grid, Rotor Shaft
2022-03-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 11.3567 | 0 | No outages (Normal operation).
2022-03-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 19.3567 | 0 | No outages (Normal operation).
2022-03-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 27.3567 | 0 | No outages (Normal operation).
2022-03-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 35.3567 | 0 | No outages (Normal operation).
2022-03-31 | 0.48 | 24 | 0 | 0 | 0 | 0.48 | 0.48 | 23.52 | 0.98 | 1 | 1 | 0 | 0 | 43.1967 | 0 | Asep Mulyana: Furnace grid Blackout A1-G1CB, A1-G3CB, BLBN 52-G1CB-52-G2CB & KGS 52-G1CB were tripped by over frequency relay energized. | Operation | Unconfirmed | Grid Blackout | A1-G1CB, A1-G3CB
2022-04-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 51.1967 | 0 | No outages (Normal operation).
2022-04-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-04-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-04-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-04-05 | 0.48 | 24 | 0 | 0 | 0.32 | 0 | 0.32 | 23.68 | 0.98667 | 1 | 0 | 0 | 0 | 95.68 | 0 | Asep Mulyana: LGS#1 shutdown for servomotor leaks | Maintenance | Shutdown | Repair Component | Servomotor
2022-04-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 119.68 | 0 | No outages (Normal operation).
2022-04-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 143.68 | 0 | No outages (Normal operation).
2022-04-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 167.68 | 0 | No outages (Normal operation).
2022-04-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-04-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-04-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-04-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-04-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-04-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-04-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-04-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-04-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-04-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-04-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-04-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-04-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-04-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-04-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-04-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-04-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-04-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-04-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-04-28 | 0.48 | 24 | 0 | 0.9 | 0 | 0 | 0 | 24 | 1 | 0.9625 | 0 | 0 | 0 | 144 | 0 | Wahyu Setiadjati: LGS#1 put on SNL for split to Aux grid | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2022-04-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-04-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-05-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-05-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-05-03 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-05-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-05-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-05-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-05-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-05-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-05-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-05-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-05-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-05-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-05-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-05-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-05-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-05-16 | 0.48 | 24 | 0 | 0.13 | 0 | 0 | 0 | 24 | 1 | 0.99458 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 put to standby for split to Thermal auxiliaries. | Standby | Put to Standby | Prepare Split to Grid | Thermal Auxiliary
2022-05-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-05-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-05-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-05-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-05-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-05-22 | 0.48 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 1 | 0.99375 | 0 | 0 | 0 | 48 | 0 | Asep Mulyana: LGS#1 put standby for split to FCE’s grid | Standby | Put to Standby | Prepare Split to Grid | FCE Grid
2022-05-23 | 0.48 | 24 | 18.5 | 0 | 0 | 0 | 18.5 | 5.5 | 0.22917 | 1 | 0 | 0 | 0 | 53.5 | 0 | Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM. | Actual Plant Outage | Shutdown | Check and Repair | Generator
2022-05-24 | 0.48 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53.5 | 0 | Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM. | Actual Plant Outage | Shutdown | Check and Repair | Generator
2022-05-25 | 0.48 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53.5 | 0 | Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM. | Actual Plant Outage | Shutdown | Check and Repair | Generator
2022-05-26 | 0.48 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 53.5 | 0 | Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM. | Actual Plant Outage | Shutdown | Check and Repair | Generator
2022-05-27 | 0.48 | 24 | 19.03 | 0 | 0 | 0 | 19.03 | 4.97 | 0.20708 | 1 | 0 | 0 | 0 | 58.47 | 0 | Asep Mulyana: LGS#1 shut down for Clean up generator stator-Rotor & General PM. | Actual Plant Outage | Shutdown | Check and Repair | Generator
2022-05-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-05-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-05-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-05-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-06-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-06-02 | 24 | 24 | 21.15 | 0 | 0 | 0 | 21.15 | 2.85 | 0.11875 | 1 | 0 | 0 | 0 | 122.85 | 0 | Wahyu Setiadjati: Total shutdown, inspection of canal lining Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check. | Actual Plant Outage | Total Shutdown | PM Check | Canal
2022-06-03 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 122.85 | 0 | Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check. | Actual Plant Outage | Shutdown | PM Check | Canal
2022-06-04 | 0.48 | 24 | 14.72 | 0 | 0 | 0 | 14.72 | 9.28 | 0.38667 | 1 | 0 | 0 | 0 | 9.28 | 0 | Asep Mulyana: LGS#1 shut down for Canal Inspection & General PM Check. | Actual Plant Outage | Shutdown | PM Check | Canal
2022-06-05 | 0.48 | 24 | 0 | 0.78 | 0 | 0 | 0 | 24 | 1 | 0.9675 | 0 | 0 | 0 | 33.28 | 0 | Asep Mulyana: LGS#1 put standby for thermal split bus | Standby | Put to Standby | Prepare Split to Grid | Thermal Bus
2022-06-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 57.28 | 0 | No outages (Normal operation).
2022-06-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 81.28 | 0 | No outages (Normal operation).
2022-06-08 | 0.48 | 24 | 0 | 0.22 | 0 | 0 | 0 | 24 | 1 | 0.99083 | 0 | 0 | 0 | 105.28 | 0 | Asep Mulyana: LGS#1 back online & supply aux grid (23:59 A1G1CB open). Outage : 0.22 hrs | Standby | Put to Standby | Back in Service to Grid | Auxiliary Grid
2022-06-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 129.28 | 0 | No outages (Normal operation).
2022-06-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 153.28 | 0 | No outages (Normal operation).
2022-06-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-06-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-06-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-06-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-06-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-06-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-06-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-06-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-06-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-06-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-06-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-06-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-06-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-06-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-06-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-06-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-06-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-06-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-06-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-06-30 | 10 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-07-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-07-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-07-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-07-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-07-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-07-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-07-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-07-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-07-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-07-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-07-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-07-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-07-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-07-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-07-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-07-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-07-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-07-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-07-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-07-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-07-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-07-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-07-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-07-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-07-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-07-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-07-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-07-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-07-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-07-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-07-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-08-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-08-02 | 0.48 | 24 | 0 | 0 | 11.9 | 0 | 11.9 | 12.1 | 0.50417 | 1 | 0 | 0 | 0 | 84.1 | 0 | Asep Mulyana: LGS#1 shutdown for Card module 64R replacement & general PM Check. | Maintenance | Shutdown | Check and Repair | Card Module 64R
2022-08-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 108.1 | 0 | No outages (Normal operation).
2022-08-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 132.1 | 0 | No outages (Normal operation).
2022-08-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 156.1 | 0 | No outages (Normal operation).
2022-08-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-08-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-08-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-08-09 | 0.48 | 24 | 0 | 0.05 | 0 | 0 | 0 | 24 | 1 | 0.99792 | 0 | 0 | 0 | 96 | 0 | Asep Mulyana: LGS#1 standby for spilt to aux grid. | Standby | Put to Standby | Prepare Split to Grid | Auxiliary Grid
2022-08-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-08-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-08-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-08-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-08-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-08-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-08-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-08-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-08-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-08-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-08-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-08-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-08-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-08-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-08-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-08-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-08-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-08-27 | 0.48 | 24 | 0 | 0 | 0 | 1.02 | 1.02 | 22.98 | 0.9575 | 1 | 1 | 0 | 0 | 22.98 | 0 | Asep Mulyana: Total Blackout Occured. BGS 52-G2, KGS 52-G1, KGS 52-G2, A1-G1, A1-G2, A1-G3, A3G1,A3G2 CB trip. Note: Thermal A2L2 suddenly Trip. | Operation | Total Blackout | Equipment Trip | A1-G1, A1-G2, A1-G3, Thermal A2L2
2022-08-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 46.98 | 0 | No outages (Normal operation).
2022-08-29 | 0.48 | 24 | 0 | 0.77 | 0 | 0 | 0 | 24 | 1 | 0.96792 | 0 | 0 | 0 | 70.98 | 0 | Wahyu Setiadjati: Swithcing | Standby | Unconfirmed | Switching | Unconfirmed
2022-08-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 94.98 | 0 | No outages (Normal operation).
2022-08-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 118.98 | 0 | No outages (Normal operation).
2022-09-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 142.98 | 0 | No outages (Normal operation).
2022-09-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 166.98 | 0 | No outages (Normal operation).
2022-09-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-09-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-09-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-09-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-09-07 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-09-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-09-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-09-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-09-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-09-12 | 0.48 | 24 | 0 | 0.67 | 0 | 0 | 0 | 24 | 1 | 0.97208 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: - LGS#1 split to FCE grid outage 0.30 hrs - LGS#1 SNL for split to Aux grid. Outage 0.37 hrs | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2022-09-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-09-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-09-15 | 12 | 24 | 16.83 | 0 | 0 | 0 | 16.83 | 7.17 | 0.29875 | 1 | 0 | 0 | 0 | 127.17 | 0 | Asep Mulyana: LGS#1 shutdown for servomotor adjust, Carbon brush replacement & General PM Check. | Actual Plant Outage | Shutdown | Repair Component | Servomotor, Carbon Brush
2022-09-16 | 0.48 | 24 | 0 | 0.13 | 9.97 | 0 | 9.97 | 14.03 | 0.58458 | 0.99073 | 0 | 0 | 0 | 141.2 | 0 | Asep Mulyana: LGS#1 back on line via line#1 to supply aux grid // KGS#2. Outage: 0.13 hrs Asep Mulyana: LGS#1 back on line to supply FCE grid (load performa test to 60 MW before split to Aux grid). Outage: 9.97 hrs | Standby, Maintenance | Unconfirmed | Back Online to Supply Grid | FCE Grid
2022-09-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-09-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-09-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-09-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-09-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-09-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-09-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-09-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-09-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-09-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-09-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-09-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-09-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-09-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-10-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-10-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-10-03 | 0.48 | 24 | 0 | 0.08 | 0 | 0 | 0 | 24 | 1 | 0.99667 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 prepare split to FCE grid | Standby | Put to Standby | Prepare Split to Grid | FCE Grid
2022-10-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-10-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-10-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-10-07 | 0.48 | 24 | 0 | 0.12 | 0 | 0 | 0 | 24 | 1 | 0.995 | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: LGS#1 prepare split to Aux grid | Standby | Put to Standby | Prepare Split to Grid | Auxiliary Grid
2022-10-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-10-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-10-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-10-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-10-12 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-10-13 | 0.48 | 24 | 0 | 0.15 | 0 | 0 | 0 | 24 | 1 | 0.99375 | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: LGS#1 SNL for split to FCE grid | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2022-10-14 | 0.48 | 24 | 0 | 0 | 0.32 | 0 | 0.32 | 23.68 | 0.98667 | 1 | 0 | 0 | 0 | 167.68 | 0 | Asep Mulyana: LGS#1 was stop via 4/CS / Emergency stop on HMI on load 30 MW due to penstock vibration check on load rejection test | Maintenance | Stop | Emergency Stop | Penstock
2022-10-15 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-10-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-10-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-10-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-10-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-10-20 | 0.48 | 24 | 0 | 0 | 3.03 | 0 | 3.03 | 20.97 | 0.87375 | 1 | 0 | 0 | 0 | 140.97 | 0 | Asep Mulyana: - LGS#1 shut down for check A1G1 CB kirk key. Outage 3.02 hrs - LGS#1 was tripped via Emergency Stop HMI Larona. Outage 0.01 hrs | Maintenance | Shutdown | Check and Repair | A1-G1
2022-10-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 164.97 | 0 | No outages (Normal operation).
2022-10-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-10-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-10-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-10-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-10-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-10-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-10-28 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 1 | 0.99583 | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: LGS#1 SNL for split to aux grid. | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2022-10-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-10-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-10-31 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-11-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-11-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-11-03 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-11-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-11-05 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 1 | 0.99583 | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 standby for prepare split to FCE grid | Standby | Put to Standby | Prepare Split to Grid | FCE Grid
2022-11-06 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-11-07 | 0.48 | 24 | 0 | 1.8 | 0 | 0 | 0 | 24 | 1 | 0.925 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: - LGS#1 put on standby due to prepare split to FCE’s grid. - LGS#1 put on standby due to prepare split to Aux grid. | Standby | Put to Standby | Prepare Split to Grid | FCE Grid; Auxiliary Grid
2022-11-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-11-09 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-11-10 | 0.48 | 24 | 0 | 0.17 | 0 | 0 | 0 | 24 | 1 | 0.99292 | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: - LGS#1 put standby for adding a delay timer (3 second) on the penstock gate limit switch. | Standby | Put to Standby | Adding Delay Timer | Penstock
2022-11-11 | 0.48 | 24 | 0 | 0.13 | 0 | 0 | 0 | 24 | 1 | 0.99458 | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: - LGS#1 standby for prepare split to FCE grid due to LGS#2 emergency shut down. - LGS#1 standby for prepare split to Auxiliary gri | Standby | Put to Standby | Prepare Split to Grid | FCE Grid
2022-11-12 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | Wahyu Setiadjati: Carbon Brush Dust Extractor
2022-11-13 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-11-14 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-11-15 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-11-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-11-17 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-11-18 | 0.48 | 24 | 0 | 0.2 | 0 | 0 | 0 | 24 | 1 | 0.99167 | 0 | 0 | 0 | 168 | 0 | Asep Mulyana: LGS#1 SNL for split to FCE grid | Standby | Speed No Load | Prepare Split to Grid | FCE Grid
2022-11-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-11-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-11-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-11-22 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-11-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-11-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-11-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-11-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-11-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-11-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-11-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-11-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-12-01 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-12-02 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-12-03 | 0.48 | 24 | 0 | 0.17 | 0 | 0 | 0 | 24 | 1 | 0.99292 | 0 | 0 | 0 | 24 | 0 | Asep Mulyana: LGS#1 put to SNL for prepared split to Auxiliary Grid | Standby | Speed No Load | Prepare Split to Grid | Auxiliary Grid
2022-12-04 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-12-05 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-12-06 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-12-07 | 0.48 | 24 | 0 | 0 | 1.78 | 0 | 1.78 | 22.22 | 0.92583 | 1 | 0 | 0 | 0 | 118.22 | 0 | Asep Mulyana: LGS#1 shutdown for carbon brush replacement. | Maintenance | Shutdown | Repair Component | Carbon Brush
2022-12-08 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 142.22 | 0 | No outages (Normal operation).
2022-12-09 | 0.48 | 24 | 0 | 0.1 | 0 | 0 | 0 | 24 | 1 | 0.99583 | 0 | 0 | 0 | 166.22 | 0 | Asep Mulyana: LGS#1 standby for split to FCE grid - LGS#1 standby for split to Aux grid | Standby | Put to Standby | Prepare Split to Grid | FCE Grid; Auxiliary Grid
2022-12-10 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-12-11 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-12-12 | 0.48 | 24 | 0 | 0.48 | 0 | 0 | 0 | 24 | 1 | 0.98 | 0 | 0 | 0 | 72 | 0 | Asep Mulyana: LGS#1 put on standby prepare split to FCE’s grid | Standby | Put to Standby | Prepare Split to Grid | FCE Grid
2022-12-13 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-12-14 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-12-15 | 8 | 24 | 7.25 | 0.12 | 0 | 0 | 7.25 | 16.75 | 0.69792 | 0.99284 | 0 | 0 | 0 | 136.75 | 0 | Asep Mulyana: LGS#1 shut down for PM Check Hira Turbine & Penstock Asep Mulyana: - LGS#2 prepare split to FCE grid - LGS#2 prepare split to aux grid | Actual Plant Outage | Shutdown | Check and Repair | Turbine, Penstock
2022-12-16 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 160.75 | 0 | No outages (Normal operation).
2022-12-17 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-12-18 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-12-19 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-12-20 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-12-21 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-12-22 | 0.48 | 24 | 0 | 0.07 | 0 | 0 | 0 | 24 | 1 | 0.99708 | 0 | 0 | 0 | 144 | 0 | Asep Mulyana: LGS#1 prepare split to Aux grid | Standby | Put to Standby | Prepare Split to Grid | Auxiliary Grid
2022-12-23 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).
2022-12-24 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 24 | 0 | No outages (Normal operation).
2022-12-25 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 48 | 0 | No outages (Normal operation).
2022-12-26 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 72 | 0 | No outages (Normal operation).
2022-12-27 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 96 | 0 | No outages (Normal operation).
2022-12-28 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 120 | 0 | No outages (Normal operation).
2022-12-29 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 144 | 0 | No outages (Normal operation).
2022-12-30 | 0.48 | 24 | 0 | 0 | 0 | 0 | 0 | 24 | 1 | 1 | 0 | 0 | 0 | 168 | 0 | No outages (Normal operation).